## Manual <75mm
SEWPCC UPGRADING/EXPANSION PROJECT
Manual Valve Schedule (Smaller than 75 mm) - General Schedule
Service / Description | Valve Type | Valve Type Number | Size (mm) | Commodity Code | Commodity | Piping Material | Remarks
PROCESS MECHANICAL
Ball valves on flushing water | Ball | V306 | ≤ 50 | FSW | Flushing Water | SS
Butterfly valves on flushing water | Butterfly | V513 | 65 | FSW | Flushing Water | SS
Check valves on flushing water | Swing check | V603 | ≤ 50 | FSW | Flushing Water | SS
Check valves on flushing water | Rubber flapper check | V609 | 65 | FSW | Flushing Water | SS
Ball valves on potable water | Ball | V307 | ≤ 65 | PW | Potable Water | SS
Ball valves on non-potable water | Ball | V300 | ≤ 50 | NPW | Non-Potable Water | CU
Butterfly valves on non-potable water | Butterfly | V513 | 65 | NPW | Non-Potable Water | SS
Check valves on non-potable water | Swing check | V600 | ≤ 50 | NPW | Non-Potable Water | CU
Check valves on non-potable water | Rubber flapper check | V609 | 65 | NPW | Non-Potable Water | SS
Check valves on secondary effluent | Rubber flapper check | V609 | 65 | SE | Secondary Effluent | SS
Ball valves on sampling service | Ball | V330 | ≤ 50 | SAM | Sample | PVC
Globe valves on sampling service | Globe | V230 | ≤ 50 | SAM | Sample | PVC
Ball valves on sodium hypochlorite service | Ball | V330 | ≤ 50 | SHC | Sodium Hypochlorite | PVC
Ball valves on sodium hydroxide service | Ball | V330 | ≤ 50 | SHD | Sodium Hydroxide | CPVC
Ball valves on ferric chloride service | Ball | V330 | ≤ 50 | FC | Ferric Chloride | PVC
Ball valves on sodium bisulphite service | Ball | V330 | ≤ 50 | SBS | Sodium Bisulphite | PVC/CPVC
Ball valves on mixed polymer service | Ball | V330 | ≤ 50 | MP | Mixed Polymer | PVC
Globe valves on mixed polymer service | Globe | V230 | ≤ 50 | MP | Mixed Polymer | PVC
Ball valves on low pressure air service | Ball | V300 | ≤ 50 | ALP | Air, Low Pressure | SS
Plug valves on sand slurry service | Plug | V400 | 65 | SNS | Sand Slurry | CS
Ball valves on ballasted sludge service | Ball | V306 | 12 | BLS | Ballasted Sludge | CS | Sampling bin inlet valves
Ball valves on high-rate clarifier sludge service | Ball | V306 | 25 | HRS | High Rate Clarifier Sludge | CS | Sample valves on cyclone overflow
Pressure gauge isolation valves | Ball | V306 | 12 | Various | Various | SS
Pressure switch isolation valves | Ball | V306 | 12 | Various | Various | SS
Pressure transmitter isolation valves | Ball | V306 | 12 | Various | Various | SS
Ball valves on drains and flushing connections | Ball | V306 | ≤ 50 | Various | Various | SS
Ball valves for various services | Ball | V306 | ≤ 50 | Various | Various | SS
Ball valves for portable air flow meter connections | Ball | V307 | 32 | ALP | Air, Low Pressure | SS
Ball valves on instrument air service | Ball | V303 | ≤ 65 | IAS | Instrument Air Supply | SS
Air release on return activated sludge service | Air Release | V752 | ≤ 65 | RAS | Return Activated Sludge | SS
Backflow preventer on various services | Backflow Preventer | V642 | ≤ 65 | Various | Various | SS | Includes replacing four existing backflow preventers in the RDT Pump Room as shown on P&ID 1-0102-PPID-S504
Ball valves on diesel fuel service | Ball | V305 | ≤ 50 | DFS | Diesel Fuel Supply | CS
Check valves on diesel fuel service | Check | V605 | ≤ 50 | DFS | Diesel Fuel Supply | CS
BUILDING MECHANICAL
Ball valves on sump discharge service | Ball | V306 | ≤ 50 | SPD | Sump Pump Discharge | SS
Check valves on sump discharge service | Check | V603 | ≤ 50 | SPD | Sump Pump Discharge | SS
Ball valves on domestic hot water | Ball | V300 | ≤ 50 | DHW | Domestic Hot Water | CU
Ball valves on domestic hot water return | Ball | V300 | ≤ 50 | DHR | Domestic Hot Water Return | CU
Ball valves on potable water | Ball | V300 | ≤ 50 | PW | Potable Water | CU
Check valves on domestic hot water return | Check | V600 | 25 | DHR | Domestic Hot Water Return | CU
Check valves on potable water | Check | V600 | 40 | PW | Potable Water | CU
Ball valves on non potable water | Ball | V300 | ≤ 65 | NPW | Non-Potable Water | CU
Plug valves on natural gas | Plug | V420 | ≤ 65 | NG | Natural Gas | CS
Ball valves on natural gas | Ball | V311 | ≤ 65 | NG | Natural Gas | CS
Ball valves on glycol service | Ball | V300 | ≤ 65 | GS | Glycol Supply | CS
Plug valves on hot water supply | Plug | V400 | ≤ 50 | HWS | Hot Water Supply | CU
Plug valves on hot water return | Plug | V400 | ≤ 50 | HWR | Hot Water Return | CU
General Notes:
1. This schedule is provided for the Contractor's convenience and shall not be taken as complete.
2. Valves to be supplied and installed under this contract unless otherwise indicated.
3. n/a = not applicable; valve supplied by others, installed under this contract.
4. Refer to the scope of pre-purchased equipment for valves that are supplied by others to be installed under this contract.
Bottom of print range

## Manual >=75mm
SEWPCC UPGRADING/EXPANSION PROJECT
Manual Valve Schedule (75 mm and Larger)
Location / Description | Tag Number | P&ID Number | Valve Type | Valve Type Number | Size (mm) | Commodity Code | Commodity | Remarks
PROCESS MECHANICAL
AREA G - HEADWORKS
Screening
Process Drain to Screens Effluent Channel | HV-G214H | 1-0102-PPID-G202 | Knife gate | V150 | 350 | PD | Process Drain
Process Drain to Screens Influent Channel | HV-G214J | 1-0102-PPID-G202 | Knife gate | V150 | 350 | PD | Process Drain
Process Drain Cross-connection | HV-G214K | 1-0102-PPID-G202 | Knife gate | V150 | 350 | PD | Process Drain
Sluice Water to Screenings Sluice | HV-G230A | 1-0102-PPID-G203 | Pinch | V905 | 100 | GE | Grit Effluent
Sluice Water from Grit Tanks 1 & 2 Effluent Channel | HV-G220A | 1-0102-PPID-G204 | Knife gate | V150 | 150 | GE | Grit Effluent
Sluice Water from Grit Tanks 3 & 4 Effluent Channel | HV-G220B | 1-0102-PPID-G204 | Knife gate | V150 | 150 | GE | Grit Effluent
Sluice Water Pump P-G221 Inlet | HV-G221A | 1-0102-PPID-G204 | Knife gate | V150 | 150 | GE | Grit Effluent
Sluice Water Pump P-G221 Outlet | CV-G221 | 1-0102-PPID-G204 | Check | V609 | 100 | GE | Grit Effluent
Sluice Water Pump P-G221 Outlet | HV-G221B | 1-0102-PPID-G204 | Knife gate | V150 | 100 | GE | Grit Effluent
Sluice Water Pump P-G222 Inlet | HV-G222A | 1-0102-PPID-G204 | Knife gate | V150 | 150 | GE | Grit Effluent
Sluice Water Pump P-G222 Outlet | CV-G222 | 1-0102-PPID-G204 | Check | V609 | 100 | GE | Grit Effluent
Sluice Water Pump P-G222 Outlet | HV-G222B | 1-0102-PPID-G204 | Knife gate | V150 | 100 | GE | Grit Effluent
Grit Removal
Grit Tank 1 Outlet | HV-G321F | 1-0102-PPID-G301 | Knife gate | V150 | 100 | GRS | Grit Slurry
Grit Tank 2 Outlet | HV-G322F | 1-0102-PPID-G301 | Knife gate | V150 | 100 | GRS | Grit Slurry
Grit Slurry Pump P-G323 Inlet | HV-G323A | 1-0102-PPID-G302 | Knife gate | V150 | 100 | GRS | Grit Slurry
Grit Slurry Pump P-G323 Outlet | CV-G323 | 1-0102-PPID-G302 | Check | V609 | 100 | GRS | Grit Slurry
Grit Slurry Pump P-G323 Outlet | HV-G323B | 1-0102-PPID-G302 | Knife gate | V150 | 100 | GRS | Grit Slurry
Grit Slurry Pump P-G324 Inlet | HV-G324A | 1-0102-PPID-G302 | Knife gate | V150 | 100 | GRS | Grit Slurry
Grit Slurry Pump P-G324 Outlet | CV-G324 | 1-0102-PPID-G302 | Check | V609 | 100 | GRS | Grit Slurry
Grit Slurry Pump P-G324 Outlet | HV-G324B | 1-0102-PPID-G302 | Knife gate | V150 | 100 | GRS | Grit Slurry
Grit Slurry Pump P-G325 Inlet | HV-G325A | 1-0102-PPID-G302 | Knife gate | V150 | 100 | GRS | Grit Slurry
Grit Slurry Pump P-G325 Outlet | CV-G325 | 1-0102-PPID-G302 | Check | V609 | 100 | GRS | Grit Slurry
Grit Slurry Pump P-G325 Outlet | HV-G325B | 1-0102-PPID-G302 | Knife gate | V150 | 100 | GRS | Grit Slurry
Grit Slurry from Pumps P-G323/P-G324 | HV-G323C | 1-0102-PPID-G302 | Knife gate | V150 | 100 | GRS | Grit Slurry
Grit Slurry from Pumps P-G325/P-G324 | HV-G325C | 1-0102-PPID-G302 | Knife gate | V150 | 100 | GRS | Grit Slurry
Grit Slurry Pumps Suction Cross-connection | HV-G323D | 1-0102-PPID-G302 | Knife gate | V150 | 100 | GRS | Grit Slurry
Grit Slurry Pumps Suction Cross-connection | HV-G325D | 1-0102-PPID-G302 | Knife gate | V150 | 100 | GRS | Grit Slurry
Grit Slurry Pump P-G335 Outlet | CV-G335A | 1-0102-PPID-G304 | Check | V609 | 100 | GRS | Grit Slurry
Grit Slurry Pump P-G335 Outlet | HV-G335B | 1-0102-PPID-G304 | Knife gate | V150 | 100 | GRS | Grit Slurry
Grit Slurry Pump P-G336 Outlet | CV-G336A | 1-0102-PPID-G304 | Check | V609 | 100 | GRS | Grit Slurry
Grit Slurry Pump P-G336 Outlet | HV-G336B | 1-0102-PPID-G304 | Knife gate | V150 | 100 | GRS | Grit Slurry
Grit Classifier GRP-G341 Drain | HV-G341D | 1-0102-PPID-G305 | Knife gate | V150 | 75 | GRS | Grit Slurry
Grit Classifier GRP-G342 Drain | HV-G342D | 1-0102-PPID-G305 | Knife gate | V150 | 75 | GRS | Grit Slurry
Grit Blower B-G353 Inlet | HV-G353A | 1-0102-PPID-G306 | Butterfly | V510 | 200 | ALP | Air, Low Pressure
Grit Blower B-G353 Outlet | CV-G353 | 1-0102-PPID-G306 | Check | N/A | 100 | ALP | Air, Low Pressure | Supplied by blower vendor.
Grit Blower B-G353 Outlet | HV-G353B | 1-0102-PPID-G306 | Butterfly | V510 | 200 | ALP | Air, Low Pressure
Grit Blower B-G354 Inlet | HV-G354A | 1-0102-PPID-G306 | Butterfly | V510 | 200 | ALP | Air, Low Pressure
Grit Blower B-G354 Outlet | CV-G354 | 1-0102-PPID-G306 | Check | N/A | 100 | ALP | Air, Low Pressure | Supplied by blower vendor.
Grit Blower B-G354 Outlet | HV-G354B | 1-0102-PPID-G306 | Butterfly | V510 | 200 | ALP | Air, Low Pressure
Wash Water
Automatic Strainer STR-G502 Inlet | HV-G535A | 1-0102-PPID-G508 | Butterfly | V500 | 150 | FSW | Flushing Water
Automatic Strainer STR-G502 Outlet | HV-G535B | 1-0102-PPID-G508 | Butterfly | V500 | 150 | FSW | Flushing Water
Automatic Strainer STR-G503 Inlet | HV-G536A | 1-0102-PPID-G508 | Butterfly | V500 | 150 | FSW | Flushing Water
Automatic Strainer STR-G503 Outlet | HV-G536B | 1-0102-PPID-G508 | Butterfly | V500 | 150 | FSW | Flushing Water
Wash Water to Screens | HV-G534C | 1-0102-PPID-G508 | Butterfly | V500 | 75 | FSW | Flushing Water
Wash Water to Screens | CV-G534 | 1-0102-PPID-G508 | Check | V609 | 75 | FSW | Flushing Water
Channel Aeration
Air Low Pressure to Screen Channel 1 | HV-G211E | 1-0102-PPID-G201 | Butterfly | V510 | 75 | ALP | Air, Low Pressure
Air Low Pressure to Screen Channel 1 | HV-G212F | 1-0102-PPID-G201 | Butterfly | V510 | 75 | ALP | Air, Low Pressure
Air Low Pressure to Screen Channel 2 | HV-G211J | 1-0102-PPID-G201 | Butterfly | V510 | 75 | ALP | Air, Low Pressure
Air Low Pressure to Screen Channel 2 | HV-G212G | 1-0102-PPID-G201 | Butterfly | V510 | 75 | ALP | Air, Low Pressure
Sump Pump Discharge | HV-G201A | 1-0102-PPID-G201 | Ball | V315 | 100 | SPD | Sump Pump Discharge
Sump Pump Discharge | HV-G201B | 1-0102-PPID-G201 | Ball | V315 | 100 | SPD | Sump Pump Discharge
Air Low Pressure to Screen Channel 3 | HV-G213E | 1-0102-PPID-G202 | Butterfly | V510 | 75 | ALP | Air, Low Pressure
Air Low Pressure to Screen Channel 3 | HV-G214E | 1-0102-PPID-G202 | Butterfly | V510 | 75 | ALP | Air, Low Pressure
Air Low Pressure to Screen Channel 4 | HV-G213G | 1-0102-PPID-G202 | Butterfly | V510 | 75 | ALP | Air, Low Pressure
Air Low Pressure to Screen Channel 4 | HV-G214G | 1-0102-PPID-G202 | Butterfly | V510 | 75 | ALP | Air, Low Pressure
Air Low Pressure to Screens Influent Channel | HV-G211F | 1-0102-PPID-G201 | Butterfly | V510 | 75 | ALP | Air, Low Pressure
Air Low Pressure to Screens Influent Channel | HV-G213F | 1-0102-PPID-G202 | Butterfly | V510 | 75 | ALP | Air, Low Pressure
Air Low Pressure to Screens Effluent Channel | HV-G212E | 1-0102-PPID-G201 | Butterfly | V510 | 75 | ALP | Air, Low Pressure
Air Low Pressure to Screens Effluent Channel | HV-G214F | 1-0102-PPID-G202 | Butterfly | V510 | 75 | ALP | Air, Low Pressure
Air Low Pressure to Grit Tanks 1 & 2 Influent Channel | HV-G353G | 1-0102-PPID-G307 | Butterfly | V510 | 100 | ALP | Air, Low Pressure
Air Low Pressure to Grit Tanks 1 & 2 Effluent Channel | HV-G353F | 1-0102-PPID-G307 | Butterfly | V510 | 150 | ALP | Air, Low Pressure
Air Low Pressure to Grit Tanks 3 & 4 Influent Channel | HV-G353D | 1-0102-PPID-G307 | Butterfly | V510 | 75 | ALP | Air, Low Pressure
Air Low Pressure to Grit Tanks 3 & 4 Influent Channel | HV-G353H | 1-0102-PPID-G307 | Butterfly | V510 | 100 | ALP | Air, Low Pressure
Air Low Pressure to Primary Clarifiers Area | HV-G353P | 1-0102-PPID-G307 | Butterfly | V510 | 300 | ALP | Air, Low Pressure
Air Low Pressure to Grit Tanks 3 & 4 Influent Channel | HV-G332J | 1-0102-PPID-G303 | Butterfly | V510 | 100 | ALP | Air, Low Pressure
Air Low Pressure to Grit Tanks 3 & 4 Influent Channel | HV-G332K | 1-0102-PPID-G303 | Butterfly | V510 | 100 | ALP | Air, Low Pressure
Air Low Pressure to Grit Tanks 3 & 4 Influent Channel | HV-G332L | 1-0102-PPID-G303 | Butterfly | V510 | 100 | ALP | Air, Low Pressure
Air Low Pressure to Grit Tanks 3 & 4 Effluent Channel | HV-G212H | 1-0102-PPID-G201 | Butterfly | V510 | 150 | ALP | Air, Low Pressure
Air Low Pressure to Grit Tanks 3 & 4 Effluent Channel | HV-G331J | 1-0102-PPID-G303 | Butterfly | V510 | 150 | ALP | Air, Low Pressure
Air Low Pressure to Grit Tanks 3 & 4 Effluent Channel | HV-G331K | 1-0102-PPID-G303 | Butterfly | V510 | 150 | ALP | Air, Low Pressure
Air Low Pressure to Grit Tanks 3 & 4 Effluent Channel | HV-G331L | 1-0102-PPID-G303 | Butterfly | V510 | 150 | ALP | Air, Low Pressure
Channel Aeration Blower B-G351 Inlet | HV-G351A | 1-0102-PPID-G307 | Butterfly | V510 | 300 | ALP | Air, Low Pressure
Channel Aeration Blower B-G351 Outlet | CV-G351 | 1-0102-PPID-G307 | Check | V618 | 300 | ALP | Air, Low Pressure
Channel Aeration Blower B-G351 Outlet | HV-G351B | 1-0102-PPID-G307 | Butterfly | V510 | 300 | ALP | Air, Low Pressure
Channel Aeration Blower B-G352 Inlet | HV-G352A | 1-0102-PPID-G307 | Butterfly | V510 | 300 | ALP | Air, Low Pressure
Channel Aeration Blower B-G352 Outlet | CV-G352 | 1-0102-PPID-G307 | Check | V618 | 300 | ALP | Air, Low Pressure
Channel Aeration Blower B-G352 Outlet | HV-G352B | 1-0102-PPID-G307 | Butterfly | V510 | 300 | ALP | Air, Low Pressure
Miscellaneous
HRCS to Primary Clarifiers Influent Channel | HV-G321G | 1-0102-PPID-G301 | Eccentric plug | V405 | 300 | HRS | High Rate Clarifier Sludge
Flushing Water to Glycol/Flushing Water Heat Exchanger | HV-G534D | 1-0102-PPID-G508 | Butterfly | V500 | 100 | FSW | Flushing Water
AREA P - PRIMARY CLARIFIERS
Primary Sludge to Sludge Holding Tanks | HV-P1092 | 1-0102-PPID-P205 | Eccentric plug | V405 | 150 | PS | Primary Sludge | Provide operator with open and close position limit switches.
Primary Sludge to Primary Sludge Fermenters Cell 4 | HV-P503E | 1-0102-PPID-P205 | Eccentric plug | V405 | 150 | PS | Primary Sludge
Primary Sludge to Primary Sludge Fermenters | HV-P503J | 1-0102-PPID-P205 | Eccentric plug | V405 | 150 | PS | Primary Sludge
FSW to Fermenters, HRC, and Chemical Building. | HV-P576A | 1-0102-PPID-P503 | Eccentric plug | V405 | 250 | FSW | Flushing Water
Process Drain from Primary Clarifiers Effluent Channel | HV-P405A | 1-0102-PPID-P103 | Eccentric plug | V405 | 100 | PD | Process Drain
AREA R - BIOREACTORS / BLOWER BUILDING
Bioreactor 1
Primary Effluent to Pre-anoxic Zone | HV-R101B | 1-0102-PPID-R101 | Knife gate | V150 | 350 | PE | Primary Effluent
Primary Effluent to Pre-anoxic Zone | HV-R101C | 1-0102-PPID-R101 | Knife gate | V150 | 350 | PE | Primary Effluent
RAS to Pre-anoxic Zone | HV-R101A | 1-0102-PPID-R101 | Knife gate | V150 | 600 | RAS | Return Activated Sludge
Fermented Sludge Filtrate to Anaerobic Zone | HV-R101D | 1-0102-PPID-R101 | Eccentric plug | V405 | 100 | FSF | Fermented Sludge Filtrate
Fermented Sludge Filtrate to Anaerobic Zone | HV-R101E | 1-0102-PPID-R101 | Eccentric plug | V405 | 100 | FSF | Fermented Sludge Filtrate
Fermented Sludge Filtrate to Anoxic Zone | HV-R102D | 1-0102-PPID-R101 | Eccentric plug | V405 | 75 | FSF | Fermented Sludge Filtrate
Fermented Sludge Filtrate to Anoxic Zone | HV-R102E | 1-0102-PPID-R101 | Eccentric plug | V405 | 75 | FSF | Fermented Sludge Filtrate
Process Drain Header | HV-R101J | 1-0102-PPID-R101 | Eccentric plug | V405 | 250 | PD | Process Drain
Air Low Pressure to IFAS Distribution Channel | HV-R104A | 1-0102-PPID-R102 | Butterfly | V514 | 150 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Distribution Channel | HV-R104B | 1-0102-PPID-R102 | Butterfly | V514 | 150 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Distribution Channel | HV-R104H | 1-0102-PPID-R102 | Butterfly | V514 | 100 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Zone | HV-R104C | 1-0102-PPID-R102 | Butterfly | V514 | 500 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Zone | HV-R104D | 1-0102-PPID-R102 | Butterfly | V514 | 200 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Zone | HV-R104E | 1-0102-PPID-R102 | Butterfly | V514 | 200 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Zone | HV-R104F | 1-0102-PPID-R102 | Butterfly | V514 | 200 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Zone | HV-R104G | 1-0102-PPID-R102 | Butterfly | V514 | 200 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Zone | HV-R104AD | 1-0102-PPID-R102 | Butterfly | V514 | 200 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Zone | HV-R104AE | 1-0102-PPID-R102 | Butterfly | V514 | 200 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Zone | HV-R104AF | 1-0102-PPID-R102 | Butterfly | V514 | 200 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Zone | HV-R104AG | 1-0102-PPID-R102 | Butterfly | V514 | 200 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Media Screens | HV-R104K | 1-0102-PPID-R102 | Butterfly | V514 | 100 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Media Screens | HV-R104L | 1-0102-PPID-R102 | Butterfly | V514 | 100 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Media Screens | HV-R104I | 1-0102-PPID-R102 | Butterfly | V514 | 75 | ALP | Air, Low Pressure
Air Low Pressure to Post Aerobic Zone | HV-R105A | 1-0102-PPID-R102 | Butterfly | V514 | 150 | ALP | Air, Low Pressure
Air Low Pressure to Post Aerobic Zone | HV-R105B | 1-0102-PPID-R102 | Butterfly | V514 | 150 | ALP | Air, Low Pressure
Air Low Pressure to Post Aerobic Zone | HV-R105C | 1-0102-PPID-R102 | Butterfly | V514 | 150 | ALP | Air, Low Pressure
Air Low Pressure to Post Aerobic Zone | HV-R105D | 1-0102-PPID-R102 | Butterfly | V514 | 150 | ALP | Air, Low Pressure
Air Low Pressure to PE Channel | HV-R220A | 1-0102-PPID-R102 | Butterfly | V514 | 200 | ALP | Air, Low Pressure
Air Low Pressure to PE Channel | HV-R220C | 1-0102-PPID-R102 | Butterfly | V514 | 150 | ALP | Air, Low Pressure
Air Low Pressure to RAS Channel | HV-R220B | 1-0102-PPID-R102 | Butterfly | V514 | 200 | ALP | Air, Low Pressure
Air Low Pressure to RAS Channel | HV-R220D | 1-0102-PPID-R102 | Butterfly | V514 | 150 | ALP | Air, Low Pressure
Bioreactor 2
Primary Effluent to Pre-anoxic Zone | HV-R111B | 1-0102-PPID-R103 | Knife gate | V150 | 350 | PE | Primary Effluent
Primary Effluent to Pre-anoxic Zone | HV-R111C | 1-0102-PPID-R103 | Knife gate | V150 | 350 | PE | Primary Effluent
RAS to Pre-anoxic Zone | HV-R111F | 1-0102-PPID-R103 | Knife gate | V150 | 600 | RAS | Return Activated Sludge
Fermented Sludge Filtrate to Anaerobic Zone | HV-R111D | 1-0102-PPID-R103 | Eccentric plug | V405 | 100 | FSF | Fermented Sludge Filtrate
Fermented Sludge Filtrate to Anaerobic Zone | HV-R111E | 1-0102-PPID-R103 | Eccentric plug | V405 | 100 | FSF | Fermented Sludge Filtrate
Fermented Sludge Filtrate to Anoxic Zone | HV-R112D | 1-0102-PPID-R103 | Eccentric plug | V405 | 75 | FSF | Fermented Sludge Filtrate
Fermented Sludge Filtrate to Anoxic Zone | HV-R112E | 1-0102-PPID-R103 | Eccentric plug | V405 | 75 | FSF | Fermented Sludge Filtrate
Process Drain Pump P-R140 Inlet | HV-R140A | 1-0102-PPID-R103 | Eccentric plug | V405 | 200 | PD | Process Drain
Process Drain Pump P-R140 Outlet | ARV-R140A | 1-0102-PPID-R103 | Air release | N/A | 25 | PD | Process Drain | To be supplied by the Process Drain Pump vendor
Process Drain Pump P-R140 Outlet | CV-R140 | 1-0102-PPID-R103 | Check | V609 | 200 | PD | Process Drain
Process Drain Pump P-R140 Outlet | HV-R140B | 1-0102-PPID-R103 | Eccentric plug | V405 | 200 | PD | Process Drain
Air Low Pressure to IFAS Distribution Channel | HV-R114A | 1-0102-PPID-R104 | Butterfly | V514 | 150 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Distribution Channel | HV-R114B | 1-0102-PPID-R104 | Butterfly | V514 | 150 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Distribution Channel | HV-R114H | 1-0102-PPID-R104 | Butterfly | V514 | 100 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Zone | HV-R114C | 1-0102-PPID-R104 | Butterfly | V514 | 500 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Zone | HV-R114D | 1-0102-PPID-R104 | Butterfly | V514 | 200 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Zone | HV-R114E | 1-0102-PPID-R104 | Butterfly | V514 | 200 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Zone | HV-R114F | 1-0102-PPID-R104 | Butterfly | V514 | 200 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Zone | HV-R114G | 1-0102-PPID-R104 | Butterfly | V514 | 200 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Zone | HV-R114AD | 1-0102-PPID-R104 | Butterfly | V514 | 200 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Zone | HV-R114AE | 1-0102-PPID-R104 | Butterfly | V514 | 200 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Zone | HV-R114AF | 1-0102-PPID-R104 | Butterfly | V514 | 200 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Zone | HV-R114AG | 1-0102-PPID-R104 | Butterfly | V514 | 200 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Media Screens | HV-R114K | 1-0102-PPID-R104 | Butterfly | V514 | 100 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Media Screens | HV-R114L | 1-0102-PPID-R104 | Butterfly | V514 | 100 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Media Screens | HV-R114I | 1-0102-PPID-R104 | Butterfly | V514 | 75 | ALP | Air, Low Pressure
Air Low Pressure to Post Aerobic Zone | HV-R115A | 1-0102-PPID-R104 | Butterfly | V514 | 150 | ALP | Air, Low Pressure
Air Low Pressure to Post Aerobic Zone | HV-R115B | 1-0102-PPID-R104 | Butterfly | V514 | 150 | ALP | Air, Low Pressure
Air Low Pressure to Post Aerobic Zone | HV-R115C | 1-0102-PPID-R104 | Butterfly | V514 | 150 | ALP | Air, Low Pressure
Air Low Pressure to Post Aerobic Zone | HV-R115D | 1-0102-PPID-R104 | Butterfly | V514 | 150 | ALP | Air, Low Pressure
Bioreactor 3
Primary Effluent to Pre-anoxic Zone | HV-R121B | 1-0102-PPID-R105 | Knife gate | V150 | 350 | PE | Primary Effluent
Primary Effluent to Pre-anoxic Zone | HV-R121C | 1-0102-PPID-R105 | Knife gate | V150 | 350 | PE | Primary Effluent
RAS to Pre-anoxic Zone | HV-R121H | 1-0102-PPID-R105 | Knife gate | V150 | 600 | RAS | Return Activated Sludge
Fermented Sludge Filtrate to Anaerobic Zone | HV-R121D | 1-0102-PPID-R105 | Eccentric plug | V405 | 100 | FSF | Fermented Sludge Filtrate
Fermented Sludge Filtrate to Anaerobic Zone | HV-R121E | 1-0102-PPID-R105 | Eccentric plug | V405 | 100 | FSF | Fermented Sludge Filtrate
Fermented Sludge Filtrate to Anoxic Zone | HV-R122D | 1-0102-PPID-R105 | Eccentric plug | V405 | 75 | FSF | Fermented Sludge Filtrate
Fermented Sludge Filtrate to Anoxic Zone | HV-R122E | 1-0102-PPID-R105 | Eccentric plug | V405 | 75 | FSF | Fermented Sludge Filtrate
Air Low Pressure to IFAS Distribution Channel | HV-R124B | 1-0102-PPID-R106 | Butterfly | V514 | 150 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Distribution Channel | HV-R124C | 1-0102-PPID-R106 | Butterfly | V514 | 150 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Distribution Channel | HV-R124H | 1-0102-PPID-R106 | Butterfly | V514 | 100 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Zone | HV-R124A | 1-0102-PPID-R106 | Butterfly | V514 | 500 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Zone | HV-R124D | 1-0102-PPID-R106 | Butterfly | V514 | 200 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Zone | HV-R124E | 1-0102-PPID-R106 | Butterfly | V514 | 200 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Zone | HV-R124F | 1-0102-PPID-R106 | Butterfly | V514 | 200 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Zone | HV-R124G | 1-0102-PPID-R106 | Butterfly | V514 | 200 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Zone | HV-R124AD | 1-0102-PPID-R106 | Butterfly | V514 | 200 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Zone | HV-R124AE | 1-0102-PPID-R106 | Butterfly | V514 | 200 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Zone | HV-R124AF | 1-0102-PPID-R106 | Butterfly | V514 | 200 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Zone | HV-R124AG | 1-0102-PPID-R106 | Butterfly | V514 | 200 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Media Screens | HV-R124K | 1-0102-PPID-R106 | Butterfly | V514 | 100 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Media Screens | HV-R124L | 1-0102-PPID-R106 | Butterfly | V514 | 100 | ALP | Air, Low Pressure
Air Low Pressure to IFAS Media Screens | HV-R125I | 1-0102-PPID-R104 | Butterfly | V514 | 75 | ALP | Air, Low Pressure
Air Low Pressure to Post Aerobic Zone | HV-R125A | 1-0102-PPID-R106 | Butterfly | V514 | 150 | ALP | Air, Low Pressure
Air Low Pressure to Post Aerobic Zone | HV-R125B | 1-0102-PPID-R106 | Butterfly | V514 | 150 | ALP | Air, Low Pressure
Air Low Pressure to Post Aerobic Zone | HV-R125C | 1-0102-PPID-R106 | Butterfly | V514 | 150 | ALP | Air, Low Pressure
Air Low Pressure to Post Aerobic Zone | HV-R125D | 1-0102-PPID-R106 | Butterfly | V514 | 150 | ALP | Air, Low Pressure
Air Low Pressure to Mixed Liquor Channel | HV-R125M | 1-0102-PPID-R106 | Butterfly | V514 | 200 | ALP | Air, Low Pressure
Miscelleaneous
Air Low Pressure to Mixed Liquor Channel | HV-R130C | 1-0102-PPID-R107 | Butterfly | V514 | 150 | ALP | Air, Low Pressure
Air Low Pressure to RAS Occasionally Aerated Section | HV-R111H | 1-0102-PPID-R108 | Butterfly | V514 | 150 | ALP | Air, Low Pressure | With torque tube to gear box outside channel.
RAS to Pre-Anoxic Zone TK-R101 | HV-R101H | 1-0102-PPID-R108 | Knife gate | V150 | 600 | RAS | Return Activated Sludge
RAS to Pre-Anoxic Zone TK-R111 | HV-R111A | 1-0102-PPID-R108 | Knife gate | V150 | 600 | RAS | Return Activated Sludge
RAS to Pre-Anoxic Zone TK-R121 | HV-R121A | 1-0102-PPID-R108 | Knife gate | V150 | 600 | RAS | Return Activated Sludge
RAS to Process Drain | HV-R400B | 1-0102-PPID-R108 | Eccentric plug | V405 | 150 | PD | Process Drain
RAS to WAS Sump | HV-R400A | 1-0102-PPID-R108 | Eccentric plug | V405 | 250 | WAS | Waste Activated Sludge
RAS to WAS Sump | HV-R400D | 1-0102-PPID-R108 | Eccentric plug | V405 | 250 | WAS | Waste Activated Sludge
RAS to RAS channel | HV-R400G | 1-0102-PPID-R108 | Knife gate | V150 | 750 | RAS | Return Activated Sludge
RAS pipe upstream tie-in to 750 mm RAS | HV-R400D | 1-0102-PPID-R108 | Eccentric plug | V405 | 450 | RAS | Return Activated Sludge
RAS to WAS Sump | HV-R300A | 1-0102-PPID-R301 | Eccentric plug | V405 | 250 | WAS | Waste Activated Sludge
WAS Mixing Pump P-R304 Inlet | HV-R304A | 1-0102-PPID-R301 | Eccentric plug | V405 | 250 | WAS | Waste Activated Sludge
WAS Mixing Pump P-R304 Outlet | HV-R304B | 1-0102-PPID-R301 | Eccentric plug | V405 | 200 | WAS | Waste Activated Sludge
WAS RDT Feed Pump P-R301 Inlet | HV-R301A | 1-0102-PPID-R301 | Eccentric plug | V405 | 150 | WAS | Waste Activated Sludge
WAS RDT Feed Pump P-R301 Outlet | CV-R301 | 1-0102-PPID-R301 | Check | V609 | 150 | WAS | Waste Activated Sludge
WAS RDT Feed Pump P-R301 Outlet | HV-R301B | 1-0102-PPID-R301 | Eccentric plug | V405 | 150 | WAS | Waste Activated Sludge
WAS RDT Feed Pump P-R302 Inlet | HV-R302A | 1-0102-PPID-R301 | Eccentric plug | V405 | 150 | WAS | Waste Activated Sludge
WAS RDT Feed Pump P-R302 Outlet | CV-R302 | 1-0102-PPID-R301 | Check | V609 | 150 | WAS | Waste Activated Sludge
WAS RDT Feed Pump P-R302 Outlet | HV-R302B | 1-0102-PPID-R301 | Eccentric plug | V405 | 150 | WAS | Waste Activated Sludge
WAS RDT Feed Pump P-R303 Inlet | HV-R303A | 1-0102-PPID-R301 | Eccentric plug | V405 | 150 | WAS | Waste Activated Sludge
WAS RDT Feed Pump P-R303 Outlet | CV-R303 | 1-0102-PPID-R301 | Check | V609 | 150 | WAS | Waste Activated Sludge
WAS RDT Feed Pump P-R303 Outlet | HV-R303B | 1-0102-PPID-R301 | Eccentric plug | V405 | 150 | WAS | Waste Activated Sludge
Flushing Water to WAS Pipe | HV-R300G | 1-0102-PPID-R301 | Eccentric plug | V405 | 100 | FSW | Flushing Water
Flushing Water Header to Bioreactors Screens | HV-R300J | 1-0102-PPID-R301 | Eccentric plug | V405 | 100 | FSW | Flushing Water
Process Drain on Pump P-R301 Outlet | HV-R301C | 1-0102-PPID-R301 | Eccentric plug | V405 | 150 | PD | Process Drain
PE Channel drain | HV-R123C | 1-0102-PPID-R105 | Ball | V315 | 75 | PD | Process Drain
Blower Building
Blower B-R201 Outlet | CV-R201 | 1-0102-PPID-R201 | Check | N/A | 350 | ALP | Air, Low Pressure | Supplied by blower vendor.
Blower B-R202 Outlet | CV-R202 | 1-0102-PPID-R201 | Check | N/A | 350 | ALP | Air, Low Pressure | Supplied by blower vendor.
Blower B-R203 Outlet | CV-R203 | 1-0102-PPID-R202 | Check | N/A | 350 | ALP | Air, Low Pressure | Supplied by blower vendor.
Blower B-R204 Outlet | CV-R204 | 1-0102-PPID-R202 | Check | N/A | 350 | ALP | Air, Low Pressure | Supplied by blower vendor.
Blower B-R205 Outlet | CV-R205 | 1-0102-PPID-R203 | Check | N/A | 350 | ALP | Air, Low Pressure | Supplied by blower vendor.
Blower B-R206 Outlet | CV-R206 | 1-0102-PPID-R203 | Check | N/A | 350 | ALP | Air, Low Pressure | Supplied by blower vendor.
Blower B-R201 Outlet | HV-R201A | 1-0102-PPID-R201 | Butterfly | V514 | 400 | ALP | Air, Low Pressure
Blower B-R202 Outlet | HV-R202A | 1-0102-PPID-R201 | Butterfly | V514 | 400 | ALP | Air, Low Pressure
Blower B-R203 Outlet | HV-R203D | 1-0102-PPID-R202 | Butterfly | V514 | 400 | ALP | Air, Low Pressure
Blower B-R204 Outlet | HV-R204D | 1-0102-PPID-R202 | Butterfly | V514 | 400 | ALP | Air, Low Pressure
Blower B-R205 Outlet | HV-R205A | 1-0102-PPID-R203 | Butterfly | V514 | 400 | ALP | Air, Low Pressure
Blower B-R206 Outlet | HV-R206A | 1-0102-PPID-R203 | Butterfly | V514 | 400 | ALP | Air, Low Pressure
Air Low Pressure to Hoar Frost | HV-R200A | 1-0102-PPID-R201 | Butterfly | V514 | 200 | ALP | Air, Low Pressure
AREA S - SECONDARY CLARIFIERS
RAS Pumps P-S108 & P-S109 Suction Cross-connection | HV-S130E | 1-0102-PPID-S104 | Knife gate | V150 | 600 | RAS | Return Activated Sludge
RAS Pumps P-S216 & P-S109 Suction Cross-connection | HV-S130F | 1-0102-PPID-S104 | Knife gate | V150 | 600 | RAS | Return Activated Sludge
Clarifier 4 RAS Outlet | HV-S140A | 1-0102-PPID-S105 | Knife gate | V150 | 600 | RAS | Return Activated Sludge
Clarifier 4 RAS Drain | HV-S140B | 1-0102-PPID-S105 | Eccentric plug | V405 | 350 | RAS | Return Activated Sludge
Clarifier 5 RAS Outlet | HV-S150A | 1-0102-PPID-S106 | Knife gate | V150 | 600 | RAS | Return Activated Sludge
Clarifier 5 RAS Drain | HV-S150B | 1-0102-PPID-S106 | Eccentric plug | V405 | 350 | RAS | Return Activated Sludge
RAS Pump P-S216 Suction | HV-S216A | 1-0102-PPID-S204 | Knife gate | V150 | 600 | RAS | Return Activated Sludge
RAS Pump P-S216 Outlet | CV-S216 | 1-0102-PPID-S204 | Check | V609 | 450 | RAS | Return Activated Sludge
RAS Pump P-S216 Outlet | HV-S216B | 1-0102-PPID-S204 | Knife gate | V150 | 450 | RAS | Return Activated Sludge
RAS Pump P-S216 Flushing Water | HV-S216C | 1-0102-PPID-S204 | Eccentric plug | V405 | 100 | FSW | Flushing Water
RAS Pump P-S217 Suction | HV-S217A | 1-0102-PPID-S205 | Knife gate | V150 | 600 | RAS | Return Activated Sludge
RAS Pump P-S217 Outlet | CV-S217 | 1-0102-PPID-S205 | Check | V609 | 400 | RAS | Return Activated Sludge
RAS Pump P-S217 Outlet | HV-S217B | 1-0102-PPID-S205 | Eccentric plug | V405 | 450 | RAS | Return Activated Sludge
RAS Pump P-S217 Flushing Water | HV-S217C | 1-0102-PPID-S205 | Eccentric plug | V405 | 100 | FSW | Flushing Water
RAS Pump P-S218 Suction | HV-S218A | 1-0102-PPID-S205 | Knife gate | V150 | 600 | RAS | Return Activated Sludge
RAS Pump P-S218 Outlet | CV-S218 | 1-0102-PPID-S205 | Check | V609 | 400 | RAS | Return Activated Sludge
RAS Pump P-S218 Outlet | HV-S218B | 1-0102-PPID-S205 | Eccentric plug | V405 | 450 | RAS | Return Activated Sludge
RAS Pump P-S218 Flushing Water | HV-S218C | 1-0102-PPID-S205 | Eccentric plug | V405 | 100 | FSW | Flushing Water
Sludge Holding Tank 3 Outlet | HV-S416A | 1-0102-PPID-S207 | Ball | V315 | 250 | STS | Southend Thickened Sludge
Sludge Holding Tank 2 Outlet | HV-S417A | 1-0102-PPID-S207 | Ball | V315 | 250 | STS | Southend Thickened Sludge
Sludge Holding Tank 1 Outlet | HV-S418A | 1-0102-PPID-S207 | Ball | V315 | 250 | STS | Southend Thickened Sludge
TFS from Pumps P-D418, P-D419, P-D420 | HV-P213E | 1-0102-PPID-S207 | Eccentric plug | V405 | 150 | STS | Southend Thickened Sludge
Sludge Transfer Pump P-S401 Inlet | HV-S401A | 1-0102-PPID-S208 | Ball | V315 | 250 | STS | Southend Thickened Sludge
Sludge Transfer Pump P-S402 Inlet | HV-S402A | 1-0102-PPID-S208 | Ball | V315 | 250 | STS | Southend Thickened Sludge
Scum Pump P-S316 Suction | HV-S316A | 1-0102-PPID-S303 | Ball | V315 | 150 | SC | Scum
Scum Pump P-S316 Outlet | HV-S316B | 1-0102-PPID-S303 | Ball | V315 | 100 | SC | Scum
Scum Pump P-S317 Suction | HV-S317A | 1-0102-PPID-S303 | Ball | V315 | 150 | SC | Scum
Scum Pump P-S317 Outlet | HV-S317B | 1-0102-PPID-S303 | Ball | V315 | 100 | SC | Scum
Scum Pump P-S316 and P-S317 Recirculation | HV-S316K | 1-0102-PPID-S303 | Ball | V315 | 100 | SC | Scum
Scum Pump P-S316 and P-S317 System Supply | HV-S317K | 1-0102-PPID-S303 | Ball | V315 | 100 | SC | Scum
Secondary Clarifier 4 Scum Trough Outlet | HV-S315E | 1-0102-PPID-S303 | Eccentric plug | V405 | 250 | SC | Scum
Secondary Clarifier 5 Scum Trough Outlet | HV-S315F | 1-0102-PPID-S303 | Eccentric plug | V405 | 250 | SC | Scum
Scum from Tank V-S307 | HV-S300F | 1-0102-PPID-S304 | Ball | V315 | 100 | SC | Scum
Scum from Tank V-S307 | HV-S300G | 1-0102-PPID-S304 | Ball | V315 | 100 | SC | Scum
Scum from Tank V-S308 | HV-S300D | 1-0102-PPID-S304 | Ball | V315 | 100 | SC | Scum
Scum from Tank V-S308 | HV-S300E | 1-0102-PPID-S304 | Ball | V315 | 100 | SC | Scum
Flushing Water Pump P-S550 Suction | HV-S550A | 1-0102-PPID-S506 | Knife gate | V150 | 250 | FSW | Flushing Water
Flood Pump P-S593 Outlet | CV-S593 | 1-0102-PPID-S508 | Check | V609 | 350 | PD | Process Drain
Flood Pump P-S593 Outlet | HV-S593A | 1-0102-PPID-S508 | Butterfly | V500 | 350 | PD | Process Drain
Flood Pump P-S594 Outlet | CV-S594 | 1-0102-PPID-S508 | Check | V609 | 350 | PD | Process Drain
Flood Pump P-S594 Outlet | HV-S594A | 1-0102-PPID-S508 | Butterfly | V500 | 350 | PD | Process Drain
Flushing Service Water to RAS Pumps and Scum Pumps | HV-S215A | 1-0102-PPID-S509 | Ball | V315 | 100 | FSW | Flushing Water
Flushing Service Water to Glycol/Flushing Water HE | HV-S663A | 1-0102-PPID-S509 | Ball | V315 | 100 | FSW | Flushing Water
Flushing Service Water to RDT | HV-S555BC | 1-0102-PPID-S509 | Butterfly | V500 | 100 | FSW | Flushing Water
Sodium Bisulphite Dispersion Pumps Suction | HV-U190A | 1-0102-PPID-U101 | Gate | N/A | 200 | FE | Final Effluent | Valve to be supplied by the hot tapping contractor to suit the application
Sodium Bisulphite Dispersion Pump P-S181 Suction | HV-S181A | 1-0102-PPID-S108 | Eccentric plug | V405 | 200 | FE | Final Effluent
Sodium Bisulphite Dispersion Pump P-S181 Outlet | CV-S181 | 1-0102-PPID-S108 | Check | V609 | 150 | FE | Final Effluent
Sodium Bisulphite Dispersion Pump P-S181 Outlet | HV-S181B | 1-0102-PPID-S108 | Eccentric plug | V405 | 150 | FE | Final Effluent
Sodium Bisulphite Dispersion Pump P-S182 Suction | HV-S182A | 1-0102-PPID-S108 | Eccentric plug | V405 | 200 | FE | Final Effluent
Sodium Bisulphite Dispersion Pump P-S182 Outlet | CV-S182 | 1-0102-PPID-S108 | Check | V609 | 150 | FE | Final Effluent
Sodium Bisulphite Dispersion Pump P-S182 Outlet | HV-S182B | 1-0102-PPID-S108 | Eccentric plug | V405 | 150 | FE | Final Effluent
Flushing Water to RDT Wash Water Booster Pumps | HV-S555B | 1-0102-PPID-S509 | Butterfly | V500 | 100 | FSW | Flushing Water
AREA K - HIGH RATE CLARIFIERS
Waste Sludge Pump P-K251 Outlet | CV-K251 | 1-0102-PPID-K203 | Check | V609 | 300 | HRS | High Rate Clarifier Sludge
Waste Sludge Pump P-K252 Outlet | CV-K252 | 1-0102-PPID-K203 | Check | V609 | 300 | HRS | High Rate Clarifier Sludge
Drain Pump P-K253 Outlet | CV-K253 | 1-0102-PPID-K203 | Check | V609 | 150 | HRS | High Rate Clarifier Sludge
Drain from HRC Train 1 Clarifier Suction | HV-K114F | 1-0102-PPID-K103 | Eccentric plug | V405 | 150 | PD | Process Drain
Drain from HRC Train 2 Clarifier Suction | HV-K124F | 1-0102-PPID-K105 | Eccentric plug | V405 | 150 | PD | Process Drain
HRC Lamella Air Scour Blower Outlet | HV-K160A | 1-0102-PPID-K108 | Butterfly | V513 | 75 | ALP | Air, Low Pressure | Supplied by HRC Vendor
Recycle Pump P-K211 Inlet | HV-K211A | 1-0102-PPID-K201 | Eccentric plug | V405 | 200 | BLS | Ballasted Sludge | Supplied by HRC Vendor
Recycle Pump P-K211 Outlet | HV-K211B | 1-0102-PPID-K201 | Eccentric plug | V405 | 200 | BLS | Ballasted Sludge | Supplied by HRC Vendor
Recycle Pump P-K212 Inlet | HV-K212A | 1-0102-PPID-K201 | Eccentric plug | V405 | 200 | BLS | Ballasted Sludge | Supplied by HRC Vendor
Recycle Pump P-K212 Outlet | HV-K212B | 1-0102-PPID-K201 | Eccentric plug | V405 | 200 | BLS | Ballasted Sludge | Supplied by HRC Vendor
Recycle Pump P-K213 Inlet | HV-K213A | 1-0102-PPID-K201 | Eccentric plug | V405 | 200 | BLS | Ballasted Sludge | Supplied by HRC Vendor
Recycle Pump P-K213 Outlet | HV-K213B | 1-0102-PPID-K201 | Eccentric plug | V405 | 200 | BLS | Ballasted Sludge | Supplied by HRC Vendor
Recycle Pump P-K221 Inlet | HV-K221A | 1-0102-PPID-K202 | Eccentric plug | V405 | 200 | BLS | Ballasted Sludge | Supplied by HRC Vendor
Recycle Pump P-K221 Outlet | HV-K221B | 1-0102-PPID-K202 | Eccentric plug | V405 | 200 | BLS | Ballasted Sludge | Supplied by HRC Vendor
Recycle Pump P-K222 Inlet | HV-K222A | 1-0102-PPID-K202 | Eccentric plug | V405 | 200 | BLS | Ballasted Sludge | Supplied by HRC Vendor
Recycle Pump P-K222 Outlet | HV-K222B | 1-0102-PPID-K202 | Eccentric plug | V405 | 200 | BLS | Ballasted Sludge | Supplied by HRC Vendor
Recycle Pump P-K222 Outlet | HV-K223A | 1-0102-PPID-K202 | Eccentric plug | V405 | 200 | BLS | Ballasted Sludge | Supplied by HRC Vendor
Recycle Pump P-K223 Outlet | HV-K223B | 1-0102-PPID-K202 | Eccentric plug | V405 | 200 | BLS | Ballasted Sludge | Supplied by HRC Vendor
Waste Sludge Pump P-K251 Inlet | HV-K251A | 1-0102-PPID-K203 | Eccentric plug | V405 | 300 | HRS | High Rate Clarifier Sludge
Waste Sludge Pump P-K251 Outlet | HV-K251B | 1-0102-PPID-K203 | Eccentric plug | V405 | 300 | HRS | High Rate Clarifier Sludge
Waste Sludge Pump P-K252 Inlet | HV-K252A | 1-0102-PPID-K203 | Eccentric plug | V405 | 300 | HRS | High Rate Clarifier Sludge
Waste Sludge Pump P-K252 Outlet | HV-K252B | 1-0102-PPID-K203 | Eccentric plug | V405 | 300 | HRS | High Rate Clarifier Sludge
Drain Pump P-K253 Inlet | HV-K253A | 1-0102-PPID-K203 | Eccentric plug | V405 | 150 | PD | Process Drain
Drain Pump P-K253 Outlet | HV-K253B | 1-0102-PPID-K203 | Eccentric plug | V405 | 150 | PD | Process Drain
Drain Pump P-K253 Recirculation | HV-K253G | 1-0102-PPID-K203 | Eccentric plug | V405 | 150 | PD | Process Drain
Flushing Water to Sludge Pump P-K251 | HV-K251C | 1-0102-PPID-K203 | Butterfly | V500 | 100 | FSW | Flushing Water
Flushing Water to Sludge Pump P-K252 | HV-K252C | 1-0102-PPID-K203 | Butterfly | V500 | 100 | FSW | Flushing Water
HRS to Primary Influent Channels | HV-K254A | 1-0102-PPID-K203 | Eccentric plug | V405 | 300 | HRS | High Rate Clarifier Sludge
HRS to Fermenters Cell No. 4 | HV-K254B | 1-0102-PPID-K203 | Eccentric plug | V405 | 300 | HRS | High Rate Clarifier Sludge
HRS to Primary Clarifiers 1 & 2 Influent Channel | HV-K254C | 1-0102-PPID-K203 | Eccentric plug | V405 | 200 | HRS | High Rate Clarifier Sludge
HRS to Primary Clarifier 3 Influent Channel | HV-K254D | 1-0102-PPID-K203 | Eccentric plug | V405 | 200 | HRS | High Rate Clarifier Sludge
Drain from HRC Train 1 Coagulation Zone to Maturation Zone | FG-K113 | 1-0102-PPID-K103 | Flap | V692 | 150 | PD | Process Drain
Drain from HRC Train 2 Coagulation Zone to Maturation Zone | FG-K123 | 1-0102-PPID-K105 | Flap | V692 | 150 | PD | Process Drain
AREA D - FERMENTERS / THICKENERS
Fermenters
Primary Sludge to PS Fermenters Train 1 Cell 1 | HV-D301A | 1-0102-PPID-D301 | Eccentric plug | V405 | 150 | PS | Primary Sludge
Ferm. Sludge Recirc. to PS Fermenters Train 1 Cell 1 | HV-D301B | 1-0102-PPID-D301 | Eccentric plug | V405 | 100 | FSL | Fermented Sludge
Ferm. Sludge Recirc. from PS Fermenters Train 1 Cell 3 | HV-D301G | 1-0102-PPID-D301 | Eccentric plug | V405 | 150 | FSL | Fermented Sludge
Ferm. Sludge to RDT Feed Pumps | HV-D301F | 1-0102-PPID-D301 | Eccentric plug | V405 | 200 | FSL | Fermented Sludge
Process Drain from PS Fermenters Train 1 Cell 4 | HV-D301D | 1-0102-PPID-D301 | Eccentric plug | V405 | 300 | PD | Process Drain
HRC sludge to PS Fermenters Train 1 Cell 4 | HV-D304B | 1-0102-PPID-D301 | Eccentric plug | V405 | 300 | HRS | High Rate Clarifier Sludge
PS Fermenters Train 1 Cell 2 to Cell 3 Drain | HV-D302A | 1-0102-PPID-D301 | Shear Gate | V160 | 200 | PS | Primary Sludge
PS Fermenters Train 1 Cell 3 to Cell 4 Drain | HV-D303A | 1-0102-PPID-D301 | Shear Gate | V160 | 200 | PS | Primary Sludge
FSW to PS | HV-D314B | 1-0102-PPID-D302 | Ball | V315 | 75 | FSW | Flushing Water
Primary Sludge to PS Fermenters Train 2 Cell 1 | HV-D311A | 1-0102-PPID-D302 | Eccentric plug | V405 | 150 | PS | Primary Sludge
Ferm. Sludge Recirc. to PS Fermenters Train 2 Cell 1 | HV-D311B | 1-0102-PPID-D302 | Eccentric plug | V405 | 100 | FSL | Fermented Sludge
Ferm. Sludge Recirc. from PS Fermenters Train 2 Cell 3 | HV-D313B | 1-0102-PPID-D302 | Eccentric plug | V405 | 150 | FSL | Fermented Sludge
Ferm. Sludge to RDT Feed Pumps | HV-D311F | 1-0102-PPID-D302 | Eccentric plug | V405 | 200 | FSL | Fermented Sludge
Process Drain from PS Fermenters Train 2 Cell 4 | HV-D311D | 1-0102-PPID-D302 | Eccentric plug | V405 | 300 | PD | Process Drain
HRC sludge to PS Fermenters Train 2 Cell 4 | HV-D314A | 1-0102-PPID-D302 | Eccentric plug | V405 | 300 | HRS | High Rate Clarifier Sludge
PS Fermenters Train 2 Cell 2 to Cell 3 Drain | HV-D312A | 1-0102-PPID-D302 | Shear Gate | V160 | 200 | PS | Primary Sludge
PS Fermenters Train 2 Cell 3 to Cell 4 Drain | HV-D313A | 1-0102-PPID-D302 | Shear Gate | V160 | 200 | PS | Primary Sludge
Ferm. Recirc. Pump P-D321 Suction | HV-D321A | 1-0102-PPID-D303 | Ball | V315 | 150 | FSL | Fermented Sludge
Ferm. Recirc. Pump P-D321 Outlet | CV-D321 | 1-0102-PPID-D303 | Check | V609 | 100 | FSL | Fermented Sludge
Ferm. Recirc. Pump P-D321 Outlet | HV-D321B | 1-0102-PPID-D303 | Eccentric plug | V405 | 100 | FSL | Fermented Sludge
Ferm. Recirc. Pump P-D321 Flushing Water | HV-D321D | 1-0102-PPID-D303 | Eccentric plug | V405 | 100 | FSW | Flushing Water
Ferm. Recirc. Pump P-D321 Flushing Water | HV-D321E | 1-0102-PPID-D303 | Eccentric plug | V405 | 100 | FSW | Flushing Water
Ferm. Recirc. Pump P-D322 Suction | HV-D322A | 1-0102-PPID-D303 | Ball | V315 | 150 | FSL | Fermented Sludge
Ferm. Recirc. Pump P-D322 Outlet | CV-D322 | 1-0102-PPID-D303 | Check | V609 | 100 | FSL | Fermented Sludge
Ferm. Recirc. Pump P-D322 Outlet | HV-D322B | 1-0102-PPID-D303 | Eccentric plug | V405 | 100 | FSL | Fermented Sludge
Ferm. Recirc. Pump P-D322 Flushing Water | HV-D322D | 1-0102-PPID-D303 | Eccentric plug | V405 | 100 | FSW | Flushing Water
Ferm. Recirc. Pump P-D322 Flushing Water | HV-D322E | 1-0102-PPID-D303 | Eccentric plug | V405 | 100 | FSW | Flushing Water
Ferm. Recirc. Pump P-D323 Suction | HV-D323A | 1-0102-PPID-D303 | Ball | V315 | 150 | FSL | Fermented Sludge
Ferm. Recirc. Pump P-D323 Outlet | CV-D323 | 1-0102-PPID-D303 | Check | V609 | 100 | FSL | Fermented Sludge
Ferm. Recirc. Pump P-D323 Outlet | HV-D323B | 1-0102-PPID-D303 | Eccentric plug | V405 | 100 | FSL | Fermented Sludge
Ferm. Recirc. Pump P-D323 Flushing Water | HV-D323D | 1-0102-PPID-D303 | Eccentric plug | V405 | 100 | FSW | Flushing Water
Ferm. Recirc. Pump P-D323 Flushing Water | HV-D323E | 1-0102-PPID-D303 | Eccentric plug | V405 | 100 | FSW | Flushing Water
Ferm. Recirc. P-D321 & P-D322 Suction Cross-connection | HV-D320A | 1-0102-PPID-D303 | Eccentric plug | V405 | 150 | FSL | Fermented Sludge
Ferm. Recirc. P-D322 & P-D323 Suction Cross-connection | HV-D320B | 1-0102-PPID-D303 | Eccentric plug | V405 | 150 | FSL | Fermented Sludge
Ferm. Recirc. P-D321 & P-D322 Outlet Cross-connection | HV-D320C | 1-0102-PPID-D303 | Eccentric plug | V405 | 100 | FSL | Fermented Sludge
Ferm. Recirc. P-D322 & P-D323 Outlet Cross-connection | HV-D320D | 1-0102-PPID-D303 | Eccentric plug | V405 | 100 | FSL | Fermented Sludge
Thickeners
WAS RDT RDT-D403 Inlet | HV-D403A | 1-0102-PPID-D402 | Eccentric plug | V405 | 150 | WAS | Waste Activated Sludge
WAS to Primary Clarifiers Influent Channel | HV-D403B | 1-0102-PPID-D402 | Eccentric plug | V405 | 150 | WAS | Waste Activated Sludge
WAS RDT RDT-D404 Inlet | HV-D404A | 1-0102-PPID-D402 | Eccentric plug | V405 | 150 | WAS | Waste Activated Sludge
WAS to Primary Clarifiers Influent Channel | HV-D404B | 1-0102-PPID-D402 | Eccentric plug | V405 | 150 | WAS | Waste Activated Sludge
TWAS Hopper TK-D403-2 Drain | HV-D403E | 1-0102-PPID-D402 | Eccentric plug | V405 | 150 | TWAS | Thickened Waste Activated Sludge
TWAS Hopper TK-D404-2 Drain | HV-D404E | 1-0102-PPID-D402 | Eccentric plug | V405 | 150 | TWAS | Thickened Waste Activated Sludge
WAS RDT RDT-D403 Foul Air | HV-D403C | 1-0102-PPID-D402 | Volume control damper | V960 | 75 | FOA | Foul Air
Flocculation Tank TK-D403-1 Foul Air | HV-D403D | 1-0102-PPID-D402 | Volume control damper | V960 | 75 | FOA | Foul Air
WAS RDT RDT-D404 Foul Air | HV-D404C | 1-0102-PPID-D402 | Volume control damper | V960 | 75 | FOA | Foul Air
Flocculation Tank TK-D404-1 Foul Air | HV-D404D | 1-0102-PPID-D402 | Volume control damper | V960 | 75 | FOA | Foul Air
TWAS Pump P-D405 Inlet | HV-D405A | 1-0102-PPID-D403 | Eccentric plug | V405 | 100 | TWAS | Thickened Waste Activated Sludge
TWAS Pump P-D405 Outlet | CV-D405 | 1-0102-PPID-D403 | Check | V609 | 100 | TWAS | Thickened Waste Activated Sludge
TWAS Pump P-D405 Outlet | HV-D405B | 1-0102-PPID-D403 | Eccentric plug | V405 | 100 | TWAS | Thickened Waste Activated Sludge
TWAS Pump P-D406 Inlet | HV-D406A | 1-0102-PPID-D403 | Eccentric plug | V405 | 100 | TWAS | Thickened Waste Activated Sludge
TWAS Pump P-D406 Outlet | CV-D406 | 1-0102-PPID-D403 | Check | V609 | 100 | TWAS | Thickened Waste Activated Sludge
TWAS Pump P-D406 Outlet | HV-D406B | 1-0102-PPID-D403 | Eccentric plug | V405 | 100 | TWAS | Thickened Waste Activated Sludge
FSL RDT Feed Pump P-D411 Inlet | HV-D411A | 1-0102-PPID-D404 | Eccentric plug | V405 | 150 | FSL | Fermented Sludge
FSL RDT Feed Pump P-D411 Outlet | CV-D411 | 1-0102-PPID-D404 | Check | V609 | 150 | FSL | Fermented Sludge
FSL RDT Feed Pump P-D411 Outlet | HV-D411B | 1-0102-PPID-D404 | Eccentric plug | V405 | 150 | FSL | Fermented Sludge
FSL RDT Feed Pump P-D412 Inlet | HV-D412A | 1-0102-PPID-D404 | Eccentric plug | V405 | 150 | FSL | Fermented Sludge
FSL RDT Feed Pump P-D412 Outlet | CV-D412 | 1-0102-PPID-D404 | Check | V609 | 150 | FSL | Fermented Sludge
FSL RDT Feed Pump P-D412 Outlet | HV-D412B | 1-0102-PPID-D404 | Eccentric plug | V405 | 150 | FSL | Fermented Sludge
FSL RDT Feed Pump P-D413 Inlet | HV-D413A | 1-0102-PPID-D405 | Eccentric plug | V405 | 150 | FSL | Fermented Sludge
FSL RDT Feed Pump P-D413 Outlet | CV-D413 | 1-0102-PPID-D405 | Check | V609 | 150 | FSL | Fermented Sludge
FSL RDT Feed Pump P-D413 Outlet | HV-D413B | 1-0102-PPID-D405 | Eccentric plug | V405 | 150 | FSL | Fermented Sludge
FSL RDT Feed Pump P-D414 Inlet | HV-D414A | 1-0102-PPID-D405 | Eccentric plug | V405 | 150 | FSL | Fermented Sludge
FSL RDT Feed Pump P-D414 Outlet | CV-D414 | 1-0102-PPID-D405 | Check | V609 | 150 | FSL | Fermented Sludge
FSL RDT Feed Pump P-D414 Outlet | HV-D414B | 1-0102-PPID-D405 | Eccentric plug | V405 | 150 | FSL | Fermented Sludge
FSL RDT RDT-D415 Inlet | HV-D415A | 1-0102-PPID-D406 | Eccentric plug | V405 | 150 | FSL | Fermented Sludge
FSL RDT RDT-D416 Inlet | HV-D416A | 1-0102-PPID-D406 | Eccentric plug | V405 | 150 | FSL | Fermented Sludge
FSL RDT RDT-D417 Inlet | HV-D417A | 1-0102-PPID-D407 | Eccentric plug | V405 | 150 | FSL | Fermented Sludge
TFS Hopper TK-D415-2 Drain | HV-D415E | 1-0102-PPID-D406 | Eccentric plug | V405 | 150 | FSL | Fermented Sludge
TFS Hopper TK-D416-2 Drain | HV-D416E | 1-0102-PPID-D406 | Eccentric plug | V405 | 150 | FSL | Fermented Sludge
TFS Hopper TK-D417-2 Drain | HV-D417E | 1-0102-PPID-D407 | Eccentric plug | V405 | 150 | FSL | Fermented Sludge
FSL RDT RDT-D415 Foul Air | HV-D415C | 1-0102-PPID-D406 | Volume control damper | V960 | 75 | FOA | Foul Air
Flocculation Tank TK-D415-1 Foul Air | HV-D415D | 1-0102-PPID-D406 | Volume control damper | V960 | 75 | FOA | Foul Air
FSL RDT RDT-D416 Foul Air | HV-D416C | 1-0102-PPID-D406 | Volume control damper | V960 | 75 | FOA | Foul Air
Flocculation Tank TK-D416-1 Foul Air | HV-D416D | 1-0102-PPID-D406 | Volume control damper | V960 | 75 | FOA | Foul Air
FSL RDT RDT-D417 Foul Air | HV-D417C | 1-0102-PPID-D407 | Volume control damper | V960 | 75 | FOA | Foul Air
Flocculation Tank TK-D417-1 Foul Air | HV-D417D | 1-0102-PPID-D407 | Volume control damper | V960 | 75 | FOA | Foul Air
Polymer Solution to WAS RDT RDT-D415 | HV-D415G | 1-0102-PPID-D406 | Ball | V330 | 75 | MP | Mixed Polymer
Polymer Solution to WAS RDT RDT-D415 | CV-D415 | 1-0102-PPID-D406 | Check | V630 | 75 | MP | Mixed Polymer
Polymer Solution to WAS RDT RDT-D416 | HV-D416G | 1-0102-PPID-D406 | Ball | V330 | 75 | MP | Mixed Polymer
Polymer Solution to WAS RDT RDT-D416 | CV-D416 | 1-0102-PPID-D406 | Check | V630 | 75 | MP | Mixed Polymer
Polymer Solution to WAS RDT RDT-D417 | HV-D417G | 1-0102-PPID-D407 | Ball | V330 | 75 | MP | Mixed Polymer
Polymer Solution to WAS RDT RDT-D417 | CV-D417 | 1-0102-PPID-D407 | Check | V630 | 75 | MP | Mixed Polymer
TFS Pump P-D418 Inlet | HV-D418A | 1-0102-PPID-D408 | Eccentric plug | V405 | 100 | TFS | Thickened Fermented Sludge
TFS Pump P-D418 Outlet | CV-D418 | 1-0102-PPID-D408 | Check | V609 | 100 | TFS | Thickened Fermented Sludge
TFS Pump P-D418 Outlet | HV-D418B | 1-0102-PPID-D408 | Eccentric plug | V405 | 100 | TFS | Thickened Fermented Sludge
TFS Pump P-D419 Inlet | HV-D419A | 1-0102-PPID-D408 | Eccentric plug | V405 | 100 | TFS | Thickened Fermented Sludge
TFS Pump P-D419 Outlet | CV-D419 | 1-0102-PPID-D408 | Check | V609 | 100 | TFS | Thickened Fermented Sludge
TFS Pump P-D419 Outlet | HV-D419B | 1-0102-PPID-D408 | Eccentric plug | V405 | 100 | TFS | Thickened Fermented Sludge
TFS Pump P-D420 Inlet | HV-D420A | 1-0102-PPID-D409 | Eccentric plug | V405 | 100 | TFS | Thickened Fermented Sludge
TFS Pump P-D420 Outlet | CV-D420 | 1-0102-PPID-D409 | Check | V609 | 100 | TFS | Thickened Fermented Sludge
TFS Pump P-D420 Outlet | HV-D420B | 1-0102-PPID-D409 | Eccentric plug | V405 | 100 | TFS | Thickened Fermented Sludge
RDT Flushing Water Booster Pump P-D431 Inlet | HV-D431A | 1-0102-PPID-D410 | Butterfly | N/A | 100 | FSW | Flushing Water | Supplied by booster pump package vendor
RDT Flushing Water Booster Pump P-D431 Outlet | CV-D431 | 1-0102-PPID-D410 | Check | N/A | 75 | FSW | Flushing Water | Supplied by booster pump package vendor
RDT Flushing Water Booster Pump P-D431 Outlet | HV-D431B | 1-0102-PPID-D410 | Ball | N/A | 75 | FSW | Flushing Water | Supplied by booster pump package vendor
RDT Flushing Water Booster Pump P-D432 Inlet | HV-D432A | 1-0102-PPID-D410 | Butterfly | N/A | 100 | FSW | Flushing Water | Supplied by booster pump package vendor
RDT Flushing Water Booster Pump P-D432 Outlet | CV-D432 | 1-0102-PPID-D410 | Check | N/A | 75 | FSW | Flushing Water | Supplied by booster pump package vendor
RDT Flushing Water Booster Pump P-D432 Outlet | HV-D432B | 1-0102-PPID-D410 | Ball | N/A | 75 | FSW | Flushing Water | Supplied by booster pump package vendor
Automatic Strainer STR-D433 Inlet | HV-D433A | 1-0102-PPID-D410 | Butterfly | V500 | 100 | FSW | Flushing Water
Automatic Strainer STR-D433 Outlet | HV-D433B | 1-0102-PPID-D410 | Butterfly | V500 | 100 | FSW | Flushing Water
Automatic Strainer STR-D434 Inlet | HV-D434A | 1-0102-PPID-D410 | Butterfly | V500 | 100 | FSW | Flushing Water
Automatic Strainer STR-D434 Outlet | HV-D434B | 1-0102-PPID-D410 | Butterfly | V500 | 100 | FSW | Flushing Water
WAS Filtrate Tank TK-D450 Outlet | HV-D450A | 1-0102-PPID-D411 | Knife gate | V150 | 200 | WSF | Waste Activated Sludge Filtrate
WAS Filtrate Tank TK-D450 Drain | HV-D450B | 1-0102-PPID-D411 | Knife gate | V150 | 200 | PD | Process Drain
Filtrate Pump Suction Header Isolation | HV-D450C | 1-0102-PPID-D411 | Knife gate | V150 | 200 | FSF | Fermented Sludge Filtrate
Filtrate Pump Discharge Header Isolation | HV-D450D | 1-0102-PPID-D411 | Knife gate | V150 | 150 | FSF | Fermented Sludge Filtrate
WAS Filtrate Pump P-D451 Inlet | HV-D451A | 1-0102-PPID-D411 | Knife gate | V150 | 200 | WSF | Waste Activated Sludge Filtrate
WAS Filtrate Pump P-D451 Outlet | CV-D451 | 1-0102-PPID-D411 | Check | V609 | 150 | WSF | Waste Activated Sludge Filtrate
WAS Filtrate Pump P-D451 Outlet | HV-D451B | 1-0102-PPID-D411 | Knife gate | V150 | 150 | WSF | Waste Activated Sludge Filtrate
WAS Filtrate to Primary Clarifiers 1 and 2 Influent Channel | HV-D451K | 1-0102-PPID-D411 | Knife gate | V150 | 100 | WSF | Waste Activated Sludge Filtrate
WAS Filtrate to Primary Clarifier 3 Influent Channel | HV-D451L | 1-0102-PPID-D411 | Knife gate | V150 | 100 | WSF | Waste Activated Sludge Filtrate
WAS Filtrate Pump P-D452 Inlet | HV-D452A | 1-0102-PPID-D411 | Knife gate | V150 | 200 | WSF | Waste Activated Sludge Filtrate
WAS Filtrate Pump P-D452 Outlet | CV-D452 | 1-0102-PPID-D411 | Check | V609 | 150 | WSF | Waste Activated Sludge Filtrate
WAS Filtrate Pump P-D452 Outlet | HV-D452B | 1-0102-PPID-D411 | Knife gate | V150 | 150 | WSF | Waste Activated Sludge Filtrate
FSL Filtrate Pump P-D461 Inlet | HV-D461A | 1-0102-PPID-D412 | Knife gate | V150 | 200 | FSF | Fermented Sludge Filtrate
FSL Filtrate Pump P-D461 Outlet | CV-D461 | 1-0102-PPID-D412 | Check | V609 | 150 | FSF | Fermented Sludge Filtrate
FSL Filtrate Pump P-D461 Outlet | HV-D461B | 1-0102-PPID-D412 | Knife gate | V150 | 150 | FSF | Fermented Sludge Filtrate
FSL Filtrate Pump P-D462 Inlet | HV-D462A | 1-0102-PPID-D412 | Knife gate | V150 | 200 | FSF | Fermented Sludge Filtrate
FSL Filtrate Pump P-D462 Outlet | CV-D462 | 1-0102-PPID-D412 | Check | V609 | 150 | FSF | Fermented Sludge Filtrate
FSL Filtrate Pump P-D462 Outlet | HV-D462B | 1-0102-PPID-D412 | Knife gate | V150 | 150 | FSF | Fermented Sludge Filtrate
FSL Filtrate Pump P-D463 Inlet | HV-D463A | 1-0102-PPID-D413 | Knife gate | V150 | 200 | FSF | Fermented Sludge Filtrate
FSL Filtrate Pump P-D463 Outlet | CV-D463 | 1-0102-PPID-D413 | Check | V609 | 150 | FSF | Fermented Sludge Filtrate
FSL Filtrate Pump P-D463 Outlet | HV-D463B | 1-0102-PPID-D413 | Knife gate | V150 | 150 | FSF | Fermented Sludge Filtrate
FSL Filtrate Pump P-D464 Inlet | HV-D464A | 1-0102-PPID-D413 | Knife gate | V150 | 200 | FSF | Fermented Sludge Filtrate
FSL Filtrate Pump P-D464 Outlet | CV-D464 | 1-0102-PPID-D413 | Check | V609 | 150 | FSF | Fermented Sludge Filtrate
FSL Filtrate Pump P-D464 Outlet | HV-D464B | 1-0102-PPID-D413 | Knife gate | V150 | 150 | FSF | Fermented Sludge Filtrate
FSL Filtrate Tank TK-D460 Outlet | HV-D460A | 1-0102-PPID-D413 | Knife gate | V150 | 250 | FSF | Fermented Sludge Filtrate
FSL Filtrate Tank TK-D460 Drain | HV-D460B | 1-0102-PPID-D413 | Knife gate | V150 | 200 | PD | Process Drain
Flushing Service Water Piping in RDT Pump Room | HV-S199L | 1-0102-PPID-G107 | Ball | V315 | 75 | FSW | Flushing Water
Flushing Service Water Piping in RDT Pump Room | HV-S199M | 1-0102-PPID-G107 | Ball | V315 | 75 | FSW | Flushing Water
Flushing Service Water Piping in RDT Pump Room | HV-S199N | 1-0102-PPID-G107 | Ball | V315 | 75 | FSW | Flushing Water
AREA T - BIOFILTER / ODOUR CONTROL
East IPS Wet Well Cover | HV-T101A | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 300 | FOA | Foul Air
West IPS Wet Well Cover | HV-T101B | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 300 | FOA | Foul Air
Screen 4 Channel | HV-T101C | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 150 | FOA | Foul Air
Screen 3 Channel | HV-T101D | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 150 | FOA | Foul Air
Screen 2 Channel | HV-T101E | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 150 | FOA | Foul Air
Screen 1 Channel | HV-T101F | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 150 | FOA | Foul Air
Influent Channel | HV-T101AB | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 200 | FOA | Foul Air
Effluent Channel | HV-T101AC | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 200 | FOA | Foul Air
Sluice | HV-T101AD | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 100 | FOA | Foul Air
Headworks odour control duct | HV-T101AJ | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 400 | FOA | Foul Air
Grit Tank TK-G331 | HV-T101G | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 250 | FOA | Foul Air
Grit Tank TK-G332 | HV-T101H | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 250 | FOA | Foul Air
Grit Tank 3 and 4 effluent channel | HV-T101AE | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 250 | FOA | Foul Air
Grit Tank 1 and 2 effluent channel | HV-T101AF | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 200 | FOA | Foul Air
Grit Tank TK-G321 | HV-T101Y | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 150 | FOA | Foul Air
Grit Tank TK-G322 | HV-T101J | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 150 | FOA | Foul Air
Grit Tank 1 and 2 inffluent channel | HV-T101AG | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 150 | FOA | Foul Air
Grit Tank 3 and 4 inffluent channel | HV-T101AH | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 150 | FOA | Foul Air
Effluent channel and sluice | HV-T101V | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 300 | FOA | Foul Air
Grit Tanks odour control duct | HV-T101AK | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 600 | FOA | Foul Air
Washer Compactor WCP-G231 | HV-T101K | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 75 | FOA | Foul Air
Washer Compactor WCP-G241 | HV-T101L | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 75 | FOA | Foul Air
Grit Classifier GRP-G341 | HV-T101M | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 75 | FOA | Foul Air
Grit Classifier GRP-G342 | HV-T101N | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 75 | FOA | Foul Air
Washer Compactors and Grit Classifiers Duct | HV-T101AL | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 150 | FOA | Foul Air
Primary Clarifier 3 Scum Hopper | HV-T101O | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 150 | FOA | Foul Air
Primary Clarifiers 1 & 2 Influent Channel | HV-T101AM | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 200 | FOA | Foul Air
Primary Clarifiers 3 Influent Channel | HV-T101AN | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 150 | FOA | Foul Air
Primary Clarifiers 1 Launders | HV-T101Q | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 150 | FOA | Foul Air
Primary Clarifiers 2 Launders | HV-T101R | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 150 | FOA | Foul Air
Primary Clarifiers 1 & 2 Scum Hopper | HV-T101S | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 150 | FOA | Foul Air
Primary Clarifiers Duct | HV-T101AP | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 250 | FOA | Foul Air
Primary Clarifiers 3 Launders | HV-T101P | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 150 | FOA | Foul Air
Primary Sludge Fermenter Train 1 | HV-T101T | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 850 | FOA | Foul Air
Primary Sludge Fermenter Train 2 | HV-T101U | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 850 | FOA | Foul Air
RDTs Duct | HV-T101AQ | 1-0102-PPID-T101 | Vol. Control Damper | V960 | 200 | FOA | Foul Air
Heater Coil Inlet | HV-T104A | 1-0102-PPID-T102 | Isolation Damper | V965 | 1200 | FOA | Foul Air
Heater Coil Outlet | HV-T104B | 1-0102-PPID-T102 | Isolation Damper | V965 | 1200 | FOA | Foul Air
Heater Coil By-pass | HV-T104C | 1-0102-PPID-T102 | Isolation Damper | V965 | 1200 | FOA | Foul Air
Glycol Recirculation Pumps Loop | HV-T105I | 1-0102-PPID-T102 | Ball | V307 | 75 | GS | Glycol Supply | Supplied by Biofilter vendor
Glycol Recirculation Pump P-T107 Inlet | HV-T107A | 1-0102-PPID-T102 | Ball | V307 | 75 | GS | Glycol Supply | Supplied by Biofilter vendor
Glycol Recirculation Pump P-T107 Outlet | CV-T107 | 1-0102-PPID-T102 | Check | V603 | 75 | GS | Glycol Supply | Supplied by Biofilter vendor
Glycol Recirculation Pump P-T107 Outlet | HV-T107B | 1-0102-PPID-T102 | Ball | V307 | 75 | GS | Glycol Supply | Supplied by Biofilter vendor
Glycol Recirculation Pump P-T108 Inlet | HV-T108A | 1-0102-PPID-T102 | Ball | V307 | 75 | GS | Glycol Supply | Supplied by Biofilter vendor
Glycol Recirculation Pump P-T108 Outlet | CV-T108 | 1-0102-PPID-T102 | Check | V603 | 75 | GS | Glycol Supply | Supplied by Biofilter vendor
Glycol Recirculation Pump P-T108 Outlet | HV-T108B | 1-0102-PPID-T102 | Ball | V307 | 75 | GS | Glycol Supply | Supplied by Biofilter vendor
Glycol Recirculation Pumps Loop | HV-T105E | 1-0102-PPID-T102 | Ball | V307 | 75 | GS | Glycol Supply | Supplied by Biofilter vendor
Glycol Recirculation Pumps Loop | HV-T105F | 1-0102-PPID-T102 | Ball | V307 | 75 | GS | Glycol Supply | Supplied by Biofilter vendor
Glycol Recirculation Pumps Loop | HV-T105G | 1-0102-PPID-T102 | Ball | V307 | 75 | GS | Glycol Supply | Supplied by Biofilter vendor
Glycol Recirculation Pumps Loop | HV-T105H | 1-0102-PPID-T102 | Ball | V307 | 75 | GS | Glycol Supply | Supplied by Biofilter vendor
Winterization System Bypass Outlet | HV-T110B | 1-0102-PPID-T103 | Isolation Damper | V965 | 1200 | FOA | Foul Air
Humidifier Tower HUM-T110 Inlet | HV-T110A | 1-0102-PPID-T103 | Isolation Damper | V965 | 900 | FOA | Foul Air
Humidifier Tower HUM-T110 Outlet | HV-T110C | 1-0102-PPID-T103 | Isolation Damper | V965 | 900 | FOA | Foul Air
Humidifier Tower HUM-T110 Drain | HV-T110E | 1-0102-PPID-T103 | Ball | V330 | 100 | PD | Process Drain | Supplied by Package Vendor
Humidifier Tower HUM-T110 Drain | HV-T110F | 1-0102-PPID-T103 | Ball | V330 | 100 | PD | Process Drain | Supplied by Package Vendor
Humidifier Tower HUM-T110 Drain | HV-T110J | 1-0102-PPID-T103 | Ball | V330 | 100 | PD | Process Drain | Supplied by Package Vendor
Humidifier Tower HUM-T110 Drain | HV-T110D | 1-0102-PPID-T103 | Ball | V330 | 100 | PD | Process Drain | Supplied by Package Vendor
Recirculation Pump P-T111 Inlet | HV-T111A | 1-0102-PPID-T104 | Ball | V330 | 100 | FOA | Foul Air | Supplied by Package Vendor
Recirculation Pump P-T111 Outlet | CV-T111 | 1-0102-PPID-T104 | Check | V609 | 100 | FOA | Foul Air | Supplied by Package Vendor
Recirculation Pump P-T111 Outlet | HV-T111B | 1-0102-PPID-T104 | Ball | V330 | 100 | FOA | Foul Air | Supplied by Package Vendor
Recirculation Pump P-T112 Inlet | HV-T112A | 1-0102-PPID-T104 | Ball | V330 | 100 | FOA | Foul Air | Supplied by Package Vendor
Recirculation Pump P-T112 Outlet | CV-T112 | 1-0102-PPID-T104 | Check | V609 | 100 | FOA | Foul Air | Supplied by Package Vendor
Recirculation Pump P-T112 Outlet | HV-T112B | 1-0102-PPID-T104 | Ball | V330 | 100 | FOA | Foul Air | Supplied by Package Vendor
Humidifier Tower Recirculation | HV-T110H | 1-0102-PPID-T104 | Ball | V330 | 100 | FOA | Foul Air | Supplied by Package Vendor
Humidifier Tower Recirculation | HV-T110I | 1-0102-PPID-T104 | Ball | V330 | 100 | FOA | Foul Air | Supplied by Package Vendor
Humidifier Tower HUM-T120 Inlet | HV-T120A | 1-0102-PPID-T105 | Isolation Damper | V965 | 900 | FOA | Foul Air
Humidifier Tower HUM-T120 Outlet | HV-T120C | 1-0102-PPID-T105 | Isolation Damper | V965 | 900 | FOA | Foul Air
Humidifier Tower HUM-T120 Drain | HV-T120E | 1-0102-PPID-T105 | Ball | V330 | 100 | PD | Process Drain | Supplied by Package Vendor
Humidifier Tower HUM-T120 Drain | HV-T120H | 1-0102-PPID-T105 | Ball | V330 | 100 | PD | Process Drain | Supplied by Package Vendor
Humidifier Tower HUM-T120 Drain | HV-T120G | 1-0102-PPID-T105 | Ball | V330 | 100 | PD | Process Drain | Supplied by Package Vendor
Humidifier Tower HUM-T120 Drain | HV-T120D | 1-0102-PPID-T105 | Ball | V330 | 100 | PD | Process Drain | Supplied by Package Vendor
Recirculation Pump P-T121 Inlet | HV-T121A | 1-0102-PPID-T106 | Ball | V330 | 100 | FOA | Foul Air | Supplied by Package Vendor
Recirculation Pump P-T121 Outlet | CV-T121 | 1-0102-PPID-T106 | Check | V609 | 100 | FOA | Foul Air | Supplied by Package Vendor
Recirculation Pump P-T121 Outlet | HV-T121B | 1-0102-PPID-T106 | Ball | V330 | 100 | FOA | Foul Air | Supplied by Package Vendor
Recirculation Pump P-T122 Inlet | HV-T122A | 1-0102-PPID-T106 | Ball | V330 | 100 | FOA | Foul Air | Supplied by Package Vendor
Recirculation Pump P-T122 Outlet | CV-T122 | 1-0102-PPID-T106 | Check | V609 | 100 | FOA | Foul Air | Supplied by Package Vendor
Recirculation Pump P-T122 Outlet | HV-T122B | 1-0102-PPID-T106 | Ball | V330 | 100 | FOA | Foul Air | Supplied by Package Vendor
Humidifier Tower Recirculation | HV-T120F | 1-0102-PPID-T106 | Ball | V330 | 100 | FOA | Foul Air | Supplied by Package Vendor
Humidifier Tower Recirculation | HV-T120I | 1-0102-PPID-T106 | Ball | V330 | 100 | FOA | Foul Air | Supplied by Package Vendor
Biofilter Microstrainer Inlet | HV-T140A | 1-0102-PPID-T107 | Ball | V307 | 75 | FSW | Flushing Water
Biofilter Microstrainer Inlet | HV-T140B | 1-0102-PPID-T107 | Ball | V307 | 75 | FSW | Flushing Water
Biofilter Microstrainer Outlet | HV-T140D | 1-0102-PPID-T107 | Ball | V307 | 75 | FSW | Flushing Water
Biofilter Microstrainer By-pass | HV-T140C | 1-0102-PPID-T107 | Ball | V307 | 75 | FSW | Flushing Water
Biofilter Microstrainer Outlet | HV-T140J | 1-0102-PPID-T107 | Ball | V307 | 75 | FSW | Flushing Water
Biofilter TK-210 Inlet | HV-T210A | 1-0102-PPID-T201 | Isolation Damper | V965 | 900 | FOA | Foul Air
Biofilter TK-210 Outlet | HV-T210B | 1-0102-PPID-T201 | Isolation Damper | V965 | 900 | FOA | Foul Air
Biofilter TK-220 Inlet | HV-T220A | 1-0102-PPID-T202 | Isolation Damper | V965 | 900 | FOA | Foul Air
Biofilter TK-220 Outlet | HV-T220B | 1-0102-PPID-T202 | Isolation Damper | V965 | 900 | FOA | Foul Air
Biofilter TK-230 Inlet | HV-T230A | 1-0102-PPID-T203 | Isolation Damper | V965 | 900 | FOA | Foul Air
Biofilter TK-230 Outlet | HV-T230B | 1-0102-PPID-T203 | Isolation Damper | V965 | 900 | FOA | Foul Air
Process Sump Pump P-T261 Outlet | CV-T261 | 1-0102-PPID-T204 | Check | V609 | 75 | SPD | Sump Pump Discharge
Process Sump Pump P-T261 Outlet | HV-T261A | 1-0102-PPID-T204 | Ball | V307 | 75 | SPD | Sump Pump Discharge
Process Sump Pump P-T262 Outlet | CV-T262 | 1-0102-PPID-T204 | Check | V609 | 75 | SPD | Sump Pump Discharge
Process Sump Pump P-T262 Outlet | HV-T262A | 1-0102-PPID-T204 | Ball | V307 | 75 | SPD | Sump Pump Discharge
Process Sump Vent | HV-T260A | 1-0102-PPID-T204 | Ball | V307 | 100 | PV | Process Vent
Process Sump Foul Air | HV-T260B | 1-0102-PPID-T204 | Ball | V307 | 100 | FOA | Foul Air
Biofilter Bypass | HV-T300A | 1-0102-PPID-T301 | Isolation Damper | V965 | 1200 | FOA | Foul Air
Biofilter Exhaust Fan EF-T301 Outlet | HV-T301A | 1-0102-PPID-T301 | Isolation Damper | V965 | 1200 | FOA | Foul Air
Biofilter Exhaust Fan EF-T302 Outlet | HV-T302A | 1-0102-PPID-T301 | Isolation Damper | V965 | 1200 | FOA | Foul Air
AREA C - CHEMICAL BUILDING / ELECTRICAL BUILDING
Sodium Bisulphite Fill | HV-C300A | 1-0102-PPID-C001 | Ball | V330 | 75 | SBS | Sodium Bisulphite
Sodium Hypochlorite Fill | HV-C200A | 1-0102-PPID-C001 | Ball | V330 | 75 | SBS | Sodium Bisulphite
Sodium Hydroxyde Fill | HV-C200B | 1-0102-PPID-C001 | Ball | V330 | 75 | SBS | Sodium Bisulphite
Ferric Chloride Fill | HV-C100A | 1-0102-PPID-C001 | Ball | V330 | 75 | SBS | Sodium Bisulphite
Flushing water | HV-C416A | 1-0102-PPID-C402 | Ball | V307 | 75 | FSW | Flushing Water
Flushing water | CV-C416 | 1-0102-PPID-C402 | Check | V609 | 75 | FSW | Flushing Water
Flushing water | HV-C416B | 1-0102-PPID-C402 | Ball | V307 | 75 | FSW | Flushing Water
Polymer to RDT-D415 | HV-C416C | 1-0102-PPID-C402 | Ball | V330 | 75 | MP | Mixed Polymer
Flushing water | HV-C417A | 1-0102-PPID-C403 | Ball | V307 | 75 | FSW | Flushing Water
Flushing water | CV-C417 | 1-0102-PPID-C403 | Check | V609 | 75 | FSW | Flushing Water
Flushing water | HV-C417B | 1-0102-PPID-C403 | Ball | V307 | 75 | FSW | Flushing Water
Polymer to RDT-D416 | HV-C417C | 1-0102-PPID-C403 | Ball | V330 | 75 | MP | Mixed Polymer
Flushing water | HV-C418A | 1-0102-PPID-C404 | Ball | V307 | 75 | FSW | Flushing Water
Flushing water | CV-C418 | 1-0102-PPID-C404 | Check | V609 | 75 | FSW | Flushing Water
Flushing water | HV-C418B | 1-0102-PPID-C404 | Ball | V307 | 75 | FSW | Flushing Water
Polymer to RDT-D417 | HV-C418C | 1-0102-PPID-C404 | Ball | V330 | 75 | MP | Mixed Polymer
Downstream MXR-C418 | HV-C415C | 1-0102-PPID-C404 | Ball | V330 | 75 | MP | Mixed Polymer
Flushing water | HV-C456A | 1-0102-PPID-C409 | Ball | V307 | 75 | FSW | Flushing Water
Flushing water | CV-C456 | 1-0102-PPID-C409 | Check | V609 | 75 | FSW | Flushing Water
Flushing water | HV-C456B | 1-0102-PPID-C409 | Ball | V307 | 75 | FSW | Flushing Water
Flushing water | HV-C457A | 1-0102-PPID-C410 | Ball | V307 | 75 | FSW | Flushing Water
Flushing water | CV-C457 | 1-0102-PPID-C410 | Check | V609 | 75 | FSW | Flushing Water
Flushing water | HV-C457B | 1-0102-PPID-C410 | Ball | V307 | 75 | FSW | Flushing Water
Flushing water | HV-C476A | 1-0102-PPID-C412 | Ball | V307 | 75 | FSW | Flushing Water
Flushing water | CV-C476 | 1-0102-PPID-C412 | Check | V609 | 75 | FSW | Flushing Water
Flushing water | HV-C476B | 1-0102-PPID-C412 | Ball | V307 | 75 | FSW | Flushing Water
Polymer to Mixed Liquor Channel | HV-C471H | 1-0102-PPID-C412 | Ball | V330 | 75 | MP | Mixed Polymer
BUILDING MECHANICAL
AREA G - HEADWORKS
Sump Pump Discharge | CV-G522 | 1-0102-PPID-G505 | Check | V604 | 75 | SPD | Sump Pump Discharge
Sump Pump Discharge | CV-G521 | 1-0102-PPID-G505 | Check | V604 | 75 | SPD | Sump Pump Discharge
Sump Pump Discharge | HV-G521A | 1-0102-PPID-G505 | Ball | V315 | 75 | SPD | Sump Pump Discharge
Sump Pump Discharge | HV-G522A | 1-0102-PPID-G505 | Ball | V315 | 75 | SPD | Sump Pump Discharge
Sump Pump Discharge | CV-G532 | 1-0102-PPID-G506 | Check | V604 | 75 | SPD | Sump Pump Discharge
Sump Pump Discharge | CV-G531 | 1-0102-PPID-G506 | Check | V604 | 75 | SPD | Sump Pump Discharge
Sump Pump Discharge | HV-G531A | 1-0102-PPID-G506 | Ball | V315 | 75 | SPD | Sump Pump Discharge
Sump Pump Discharge | HV-G532A | 1-0102-PPID-G506 | Ball | V315 | 75 | SPD | Sump Pump Discharge
HC-G620-2 Feed Isolation | HV-G620C | 1-0102-PPID-G608 | Ball | V315 | 100 | GS | Glycol Supply
HC-G620-2 Return Isolation | HV-G620D | 1-0102-PPID-G608 | Ball | V315 | 100 | GR | Glycol Return
HC-G620-2 Bypass Balancing | HV-G620A | 1-0102-PPID-G608 | Balancing | V472 | 100 | GR | Glycol Return
HC-G620-2 Balancing | HV-G620B | 1-0102-PPID-G608 | Balancing | V472 | 100 | GR | Glycol Return
HC-G620-1 Feed Isolation | HV-G620G | 1-0102-PPID-G608 | Ball | V315 | 75 | GS | Glycol Supply
HC-G620-1 Return Isolation | HV-G620H | 1-0102-PPID-G608 | Ball | V315 | 75 | GR | Glycol Return
HC-G620-1 Balancing | HV-G620J | 1-0102-PPID-G608 | Balancing | V472 | 75 | GR | Glycol Return
HC-G610-2 Feed Isolation | HV-G610M | 1-0102-PPID-G617 | Ball | V315 | 75 | GS | Glycol Supply
HC-G610-2 Return Isolation | HV-G610J | 1-0102-PPID-G617 | Ball | V315 | 75 | GR | Glycol Return
HC-G610-2 Bypass Balancing | HV-G610G | 1-0102-PPID-G617 | Balancing | V472 | 75 | GR | Glycol Return
HC-G610-2 Balancing | HV-G610H | 1-0102-PPID-G617 | Balancing | V472 | 75 | GR | Glycol Return
HC-G610-1 Feed Isolation | HV-G610A | 1-0102-PPID-G617 | Ball | V315 | 75 | GS | Glycol Supply
HC-G610-1 Return Isolation | HV-G610B | 1-0102-PPID-G617 | Ball | V315 | 75 | GR | Glycol Return
HC-G610-1 Balancing | HV-G610C | 1-0102-PPID-G617 | Balancing | V472 | 75 | GR | Glycol Return
HC-G630-2 Feed Isolation | HV-G630M | 1-0102-PPID-G618 | Ball | V315 | 75 | GS | Glycol Supply
HC-G630-2 Return Isolation | HV-G630J | 1-0102-PPID-G618 | Ball | V315 | 75 | GR | Glycol Return
HC-G630-2 Bypass Balancing | HV-G630G | 1-0102-PPID-G618 | Balancing | V472 | 75 | GR | Glycol Return
HC-G630-2 Balancing | HV-G630H | 1-0102-PPID-G618 | Balancing | V472 | 75 | GR | Glycol Return
HC-G630-1 Feed Isolation | HV-G630A | 1-0102-PPID-G618 | Ball | V315 | 75 | GS | Glycol Supply
HC-G630-1 Return Isolation | HV-G630B | 1-0102-PPID-G618 | Ball | V315 | 75 | GR | Glycol Return
HC-G630-1 Balancing | HV-G630C | 1-0102-PPID-G618 | Balancing | V472 | 75 | GR | Glycol Return
P-G677 Suction Isolation | HV-G677A | 1-0102-PPID-G623 | Ball | V315 | 75 | CDS | Condensing Water Supply
P-G677 Discharge Isolation | HV-G677B | 1-0102-PPID-G623 | Ball | V315 | 75 | CDS | Condensing Water Supply
P-G677 Discharge Check | CV-G677 | 1-0102-PPID-G623 | Tripple Duty | V475 | 75 | CDS | Condensing Water Supply
P-G678 Suction Isolation | HV-G678A | 1-0102-PPID-G623 | Ball | V315 | 75 | CDS | Condensing Water Supply
P-G678 Discharge Isolation | HV-G678B | 1-0102-PPID-G623 | Ball | V315 | 75 | CDS | Condensing Water Supply
P-G678 Discharge Check | CV-G678 | 1-0102-PPID-G623 | Tripple Duty | V475 | 75 | CDS | Condensing Water Supply
Flushing Water to heat exchanger HE-G673 | BVA-G673 | 1-0102-PPID-G623 | Check | V604 | 100 | FSW | Flushing Water
HE-G673 Flushing Feed Isolation | HV-G673B | 1-0102-PPID-G623 | Ball | V315 | 100 | FSW | Flushing Water
HE-G673 Glycol Isolation | HV-G673A | 1-0102-PPID-G623 | Ball | V315 | 100 | GR | Glycol Return
HE-G673 Glycol Isolation | HV-G673C | 1-0102-PPID-G623 | Ball | V315 | 100 | GR | Glycol Return
TV-G6731 Isolation | HV-G673D | 1-0102-PPID-G623 | Ball | V315 | 100 | FSW | Flushing Water
TV-G6731 Isolation | HV-G673E | 1-0102-PPID-G623 | Ball | V315 | 100 | FSW | Flushing Water
TV-G6739-2 Isolation | HV-G673G | 1-0102-PPID-G623 | Ball | V315 | 100 | FSW | Flushing Water
TV-G6761 Isolation | HV-G675K | 1-0102-PPID-G623 | Ball | V315 | 100 | FSW | Flushing Water
TV-G6761 Isolation | HV-G675J | 1-0102-PPID-G623 | Ball | V315 | 100 | FSW | Flushing Water
Heat Pump Condenser Water | HV-G676C | 1-0102-PPID-G623 | Balancing | V472 | 75 | CDR | Condensing Water Return
Heat Pump Condenser Water | HV-G675C | 1-0102-PPID-G623 | Balancing | V472 | 75 | CDR | Condensing Water Return
Heat Pump Conderser Loop Isolation | HV-G676B | 1-0102-PPID-G623 | Ball | V315 | 75 | FSW | Flushing Water
TV-G6761 Bypass | HV-G676K | 1-0102-PPID-G623 | Ball | V315 | 100 | FSW | Flushing Water
TV-G6761 Isolation | HV-G676J | 1-0102-PPID-G623 | Ball | V315 | 100 | FSW | Flushing Water
P-G674 Suction Isolation | HV-G674A | 1-0102-PPID-G623 | Ball | V315 | 100 | GS | Glycol Supply
P-G674 Discharge Isolation | HV-G674B | 1-0102-PPID-G623 | Ball | V315 | 100 | GS | Glycol Supply
P-G674 Discharge Check | CV-G674 | 1-0102-PPID-G623 | Tripple Duty | V475 | 100 | GS | Glycol Supply
FIT-G6621 Isolation | HV-G660J | 1-0102-PPID-G624 | Ball | V315 | 150 | HWS | Hot Water Supply
FIT-G6621 Isolation | HV-G660K | 1-0102-PPID-G624 | Ball | V315 | 150 | HWS | Hot Water Supply
P-G660 Suction Isolation | HV-G660A | 1-0102-PPID-G624 | Ball | V315 | 150 | HWS | Hot Water Supply
P-G660 Discharge Isolation | HV-G660B | 1-0102-PPID-G624 | Ball | V315 | 150 | HWS | Hot Water Supply
P-G660 Discharge Check | CV-G660 | 1-0102-PPID-G624 | Tripple Duty | V475 | 150 | HWS | Hot Water Supply
P-G661 Suction Isolation | HV-G661A | 1-0102-PPID-G624 | Ball | V315 | 150 | HWS | Hot Water Supply
P-G661 Discharge Isolation | HV-G661B | 1-0102-PPID-G624 | Ball | V315 | 150 | HWS | Hot Water Supply
P-G661 Discharge Check | CV-G661 | 1-0102-PPID-G624 | Tripple Duty | V475 | 150 | HWS | Hot Water Supply
Primary Loop Isolation | HV-G660H | 1-0102-PPID-G624 | Ball | V315 | 150 | HWS | Hot Water Supply
Primary Loop Isolation | HV-G661H | 1-0102-PPID-G624 | Ball | V315 | 150 | HWR | Hot Water Return
Primary Loop Balancing | HV-G661J | 1-0102-PPID-G624 | Balancing | V472 | 150 | HWR | Hot Water Return
Primary Loop Isolation | HV-G661K | 1-0102-PPID-G624 | Ball | V315 | 150 | HWR | Hot Water Return
P-G665 Suction Isolation | HV-G665A | 1-0102-PPID-G625 | Ball | V315 | 150 | GS | Glycol Supply
P-G665 Discharge Isolation | HV-G665B | 1-0102-PPID-G625 | Ball | V315 | 150 | GS | Glycol Supply
P-G665 Discharge Check | CV-G665 | 1-0102-PPID-G625 | Tripple Duty | V475 | 150 | GS | Glycol Supply
P-G666 Suction Isolation | HV-G666A | 1-0102-PPID-G625 | Ball | V315 | 150 | GS | Glycol Supply
P-G666 Discharge Isolation | HV-G666B | 1-0102-PPID-G625 | Ball | V315 | 150 | GS | Glycol Supply
P-G666 Discharge Check | CV-G666 | 1-0102-PPID-G625 | Tripple Duty | V475 | 150 | GS | Glycol Supply
HE-G663 Glycol Isolation | HV-G663P | 1-0102-PPID-G625 | Ball | V315 | 150 | GR | Glycol Return
HE-G663 Glycol Isolation | HV-G663A | 1-0102-PPID-G625 | Ball | V315 | 150 | GS | Glycol Supply
HE-G663 Hot Water Isolation | HV-G663C | 1-0102-PPID-G625 | Ball | V315 | 150 | HWS | Hot Water Supply
HE-G663 Hot Water Isolation | HV-G663F | 1-0102-PPID-G625 | Ball | V315 | 150 | HWR | Hot Water Return
HE-G663 Bypass Balancing | HV-G663D | 1-0102-PPID-G625 | Balancing | V472 | 150 | HWR | Hot Water Return
HE-G663 Balancing | HV-G663E | 1-0102-PPID-G625 | Balancing | V472 | 150 | HWR | Hot Water Return
AREA P - PRIMARY CLARIFIERS
AREA R - BIOREACTORS / BLOWER BUILDING
Glycol Pump Discharge | HV-R610A | 1-0102-PPID-R603 | Ball | V315 | 75 | GS | Glycol Supply
Glycol Pump Suction | HV-R610B | 1-0102-PPID-R603 | Ball | V315 | 75 | GR | Glycol Return
Glycol Pump Discharge | HV-R626C | 1-0102-PPID-R604 | Ball | V315 | 75 | GS | Glycol Supply
Glycol Pump Discharge | HV-R626F | 1-0102-PPID-R604 | Ball | V315 | 75 | GS | Glycol Supply
Glycol Pump Discharge | CV-R626 | 1-0102-PPID-R604 | Check | V604 | 75 | GS | Glycol Supply
Glycol Pump Suction | HV-R626B | 1-0102-PPID-R604 | Ball | V315 | 75 | GR | Glycol Return
Glycol Pump Diverting | HV-R626A | 1-0102-PPID-R604 | Balancing | V472 | 75 | GR | Glycol Supply
Glycol Pump Suction | HV-R626D | 1-0102-PPID-R604 | Balancing | V472 | 75 | GR | Glycol Supply
Glycol Pump Suction | HV-R626E | 1-0102-PPID-R604 | Ball | V315 | 75 | GR | Glycol Supply
Sump Pump Discharge | CV-R501 | 1-0102-PPID-R501 | Check | V604 | 75 | SPD | Sump Pump Discharge
Sump Pump Discharge | CV-R502 | 1-0102-PPID-R501 | Check | V604 | 75 | SPD | Sump Pump Discharge
Sump Pump Discharge | HV-R501A | 1-0102-PPID-R501 | Ball | V315 | 75 | SPD | Sump Pump Discharge
Sump Pump Discharge | HV-R502A | 1-0102-PPID-R501 | Ball | V315 | 75 | SPD | Sump Pump Discharge
Bioreactor 1 Foul Air Suction | HV-R101G | 1-0102-PPID-R601 | Vol. Control Damper | V960 | 600 | FOA | Foul Air
Bioreactor 2 Foul Air Suction | HV-R111G | 1-0102-PPID-R601 | Vol. Control Damper | V960 | 600 | FOA | Foul Air
Bioreactor 3 Foul Air Suction | HV-R121G | 1-0102-PPID-R601 | Vol. Control Damper | V960 | 600 | FOA | Foul Air
Primary Effluent Channel Foul Air Suction | HV-R101N | 1-0102-PPID-R601 | Vol. Control Damper | V960 | 300 | FOA | Foul Air
Primary Effluent Channel Foul Air Suction | HV-R111L | 1-0102-PPID-R601 | Vol. Control Damper | V960 | 300 | FOA | Foul Air
Primary Effluent Channel Foul Air Suction | HV-R121L | 1-0102-PPID-R601 | Vol. Control Damper | V960 | 300 | FOA | Foul Air
RAS Effluent Channel Foul Air Suction | HV-R101M | 1-0102-PPID-R601 | Vol. Control Damper | V960 | 250 | FOA | Foul Air
RAS Effluent Channel Foul Air Suction | HV-R111K | 1-0102-PPID-R601 | Vol. Control Damper | V960 | 250 | FOA | Foul Air
RAS Effluent Channel Foul Air Suction | HV-R121M | 1-0102-PPID-R601 | Vol. Control Damper | V960 | 250 | FOA | Foul Air
WAS Sump Foul Air Suction | HV-R101Q | 1-0102-PPID-R601 | Vol. Control Damper | V960 | 250 | FOA | Foul Air
EF-R601 Outlet | HV-R601A | 1-0102-PPID-R602 | Isolation Damper | V965 | 1000 | FOA | Foul Air
EF-R602 Outlet | HV-R602A | 1-0102-PPID-R602 | Isolation Damper | V965 | 1000 | FOA | Foul Air
AREA S - SECONDARY CLARIFIERS
Glycol Pump Discharge | CV-S664 | 1-0102-PPID-S627 | Triple Duty | V475 | 100 | GS | Glycol Supply
Glycol Pump Suction | HV-S664A | 1-0102-PPID-S627 | Ball | V315 | 100 | GR | Glycol Return
Glycol Pump Discharge | HV-S664B | 1-0102-PPID-S627 | Ball | V315 | 100 | GS | Glycol Supply
Flushing Water Intake | HV-S663C | 1-0102-PPID-S627 | Ball | V315 | 100 | FSW | Flushing Water
Glycol Return | HV-S663D | 1-0102-PPID-S627 | Ball | V315 | 100 | GR | Glycol Return
Glycol Return | HV-S663E | 1-0102-PPID-S627 | Ball | V315 | 100 | GR | Glycol Return
Flushing Water Return | HV-S663F | 1-0102-PPID-S627 | Ball | V315 | 100 | FSW | Flushing Water
Flushing Water Intake | BVA-S663A | 1-0102-PPID-S627 | Check | V604 | 100 | FSW | Flushing Water
Glycol Supply to AHU-S630 | HV-S630A | 1-0102-PPID-S622 | Ball | V315 | 75 | GS | Glycol Supply
Glycol Return from AHU-S630 | HV-S630B | 1-0102-PPID-S622 | Ball | V315 | 75 | GR | Glycol Return
Glycol Return from AHU-S630 | HV-S630D | 1-0102-PPID-S622 | Balancing | V472 | 75 | GR | Glycol Return
Glycol Supply to AHU-S650 | HV-S650A | 1-0102-PPID-S623 | Ball | V315 | 75 | GS | Glycol Supply
Glycol Return from AHU-S650 | HV-S650B | 1-0102-PPID-S623 | Ball | V315 | 75 | GR | Glycol Return
Glycol Return from AHU-S650 | HV-S650D | 1-0102-PPID-S623 | Balancing | V472 | 75 | GR | Glycol Return
Flushing Water Intake | HV-S674A | 1-0102-PPID-S627 | Ball | V315 | 100 | FSW | Flushing Water
Flushing Water drain from Automatic Strainer | HV-S674E | 1-0102-PPID-S627 | Ball | V315 | 100 | FSW | Flushing Water
Flushing Water Intake | HV-S674F | 1-0102-PPID-S627 | Ball | V315 | 100 | FSW | Flushing Water
Flushing Water Intake | HV-S673G | 1-0102-PPID-S627 | Ball | V315 | 100 | FSW | Flushing Water
Flushing Water drain from Automatic Strainer | HV-S673J | 1-0102-PPID-S627 | Ball | V315 | 100 | FSW | Flushing Water
Flushing Water Intake | HV-S673K | 1-0102-PPID-S627 | Ball | V315 | 100 | FSW | Flushing Water
AREA U - UV DISINFECTION BUILDING
AREA K - HIGH RATE CLARIFIERS
Glycol Supply to AHU-K610 | HV-K610A | 1-0102-PPID-K601 | Balancing | V472 | 100 | GS | Glycol Supply
Glycol Return from AHU-K610 | HV-K610B | 1-0102-PPID-K601 | Balancing | V472 | 100 | GR | Glycol Return
Glycol Supply to AHU-K610 | HV-K610C | 1-0102-PPID-K601 | Ball | V315 | 100 | GS | Glycol Supply
Glycol Return from AHU-K610 | HV-K610D | 1-0102-PPID-K601 | Ball | V315 | 100 | GR | Glycol Return
Glycol Supply to AHU-K620 | HV-K620A | 1-0102-PPID-K602 | Balancing | V472 | 65 | GS | Glycol Supply
Glycol Return from AHU-K620 | HV-K620B | 1-0102-PPID-K602 | Balancing | V472 | 65 | GR | Glycol Return
Glycol Supply to AHU-K620 | HV-K620C | 1-0102-PPID-K602 | Ball | V315 | 65 | GS | Glycol Supply
Glycol Return from AHU-K620 | HV-K620D | 1-0102-PPID-K602 | Ball | V315 | 65 | GR | Glycol Return
Glycol Supply to AHU-K630 | HV-K630A | 1-0102-PPID-K603 | Balancing | V472 | 65 | GS | Glycol Supply
Glycol Return from AHU-K630 | HV-K630B | 1-0102-PPID-K603 | Balancing | V472 | 65 | GR | Glycol Return
Glycol Supply to AHU-K630 | HV-K630C | 1-0102-PPID-K603 | Ball | V315 | 65 | GS | Glycol Supply
Glycol Return from AHU-K630 | HV-K630D | 1-0102-PPID-K603 | Ball | V315 | 65 | GR | Glycol Return
Glycol Supply to AHU-K640 | HV-K640A | 1-0102-PPID-K604 | Balancing | V472 | 38 | GS | Glycol Supply
Glycol Return from AHU-K640 | HV-K640B | 1-0102-PPID-K604 | Balancing | V472 | 38 | GR | Glycol Return
Glycol Supply to AHU-K640 | HV-K640C | 1-0102-PPID-K604 | Ball | V315 | 38 | GS | Glycol Supply
Glycol Return from AHU-K640 | HV-K640D | 1-0102-PPID-K604 | Ball | V315 | 38 | GR | Glycol Return
Hot Water Pump Discharge Valve | CV-K660 | 1-0102-PPID-K605 | Triple Duty | V475 | 100 | HWS | Hot Water Supply
Hot Water Pump Discharge Valve | CV-K661 | 1-0102-PPID-K605 | Triple Duty | V475 | 100 | HWS | Hot Water Supply
Hot Water Pump Suction Isolation Valve | HV-K660A | 1-0102-PPID-K605 | Ball | V315 | 100 | HWS | Hot Water Supply
Hot Water Pump Discharge Isolation Valve | HV-K660B | 1-0102-PPID-K605 | Ball | V315 | 100 | HWS | Hot Water Supply
Flow Element Isolation Upstream | HV-K660J | 1-0102-PPID-K605 | Ball | V315 | 100 | HWS | Hot Water Supply
Flow Element Isolation Downstream | HV-K660K | 1-0102-PPID-K605 | Ball | V315 | 100 | HWS | Hot Water Supply
Hot Water Supply Main Line Isolation | HV-K660H | 1-0102-PPID-K605 | Ball | V315 | 100 | HWR | Hot Water Return
Hot Water Return Main Line Balancing | HV-K661J | 1-0102-PPID-K605 | Balancing | V500 | 100 | HWS | Hot Water Supply
Hot Water Return Secondary Isolation | HV-K661K | 1-0102-PPID-K605 | Ball | V315 | 100 | HWR | Hot Water Return
Hot Water Return Main Line Isolation | HV-K661H | 1-0102-PPID-K605 | Ball | V315 | 100 | HWR | Hot Water Return
Hot Water Pump Suction Isolation Valve | HV-K661A | 1-0102-PPID-K605 | Ball | V315 | 100 | HWS | Hot Water Supply
Hot Water Pump Discharge Isolation Valve | HV-K661B | 1-0102-PPID-K605 | Ball | V315 | 100 | HWS | Hot Water Supply
Glycol Pump Discharge Check Valve | CV-K665 | 1-0102-PPID-K606 | Triple Duty | V475 | 100 | HWS | Hot Water Supply
Glycol Pump Discharge Check Valve | CV-K666 | 1-0102-PPID-K606 | Triple Duty | V475 | 100 | HWS | Hot Water Supply
Glycol Supply from Heat Exchanger | HV-K663A | 1-0102-PPID-K606 | Ball | V315 | 100 | GS | Glycol Supply
Glycol Return to Heat Exchanger | HV-K663P | 1-0102-PPID-K606 | Ball | V315 | 100 | GR | Glycol Return
Hot Water Return from Heat Exchanger | HV-K663F | 1-0102-PPID-K606 | Ball | V315 | 100 | HWR | Hot Water Return
Hot Water Supply to Heat Exchanger | HV-K663C | 1-0102-PPID-K606 | Ball | V315 | 100 | HWS | Hot Water Supply
Heat Exchanger Balancing Valve | HV-K663E | 1-0102-PPID-K606 | Balancing | V472 | 100 | HWS | Hot Water Supply
Hot Water Bypass Balancing Valve | HV-K663D | 1-0102-PPID-K606 | Balancing | V472 | 100 | HWR | Hot Water Return
Glycol Pump Suction Isolation | HV-K665A | 1-0102-PPID-K606 | Ball | V315 | 100 | HWS | Hot Water Supply
Glycol Pump Discharge Isolation | HV-K665B | 1-0102-PPID-K606 | Ball | V315 | 100 | HWS | Hot Water Supply
Glycol Pump Suction Isolation | HV-K666A | 1-0102-PPID-K606 | Ball | V315 | 100 | GS | Glycol Supply
Glycol Pump Discharge Isolation | HV-K666B | 1-0102-PPID-K606 | Ball | V315 | 100 | HWS | Hot Water Supply
AREA D - FERMENTERS / THICKENERS
AREA T - BIOFILTER / ODOUR CONTROL
AREA C - CHEMICAL BUILDING / ELECTRICAL BUILDING
Sump Pump Discharge | CV-C501 | 1-0102-PPID-C502 | Check | V604 | 75 | SPD | Sump Pump Discharge
Sump Pump Discharge | CV-C502 | 1-0102-PPID-C502 | Check | V604 | 75 | SPD | Sump Pump Discharge
Sump Pump Discharge | HV-C501A | 1-0102-PPID-C502 | Ball | V315 | 75 | SPD | Sump Pump Discharge
Sump Pump Discharge | HV-C502A | 1-0102-PPID-C502 | Ball | V315 | 75 | SPD | Sump Pump Discharge
Potable water supply from City of Winnipeg watermain | HV-C530G | 1-0102-PPID-C503 | Ball | V315 | 100 | PW | Potable Water
Potable water supply from City of Winnipeg watermain | HV-C530H | 1-0102-PPID-C503 | Ball | V315 | 100 | PW | Potable Water
Potable water supply from City of Winnipeg watermain | HV-C530I | 1-0102-PPID-C503 | Ball | V315 | 100 | PW | Potable Water
Potable water supply from City of Winnipeg watermain | HV-C530J | 1-0102-PPID-C503 | Ball | V315 | 100 | PW | Potable Water
Natural gas supply | HV-C511B | 1-0102-PPID-C505 | Lubricated Plug | V422 | 100 | NG | Natural Gas
Natural gas supply | HV-C511C | 1-0102-PPID-C505 | Lubricated Plug | V422 | 100 | NG | Natural Gas
Natural gas supply | HV-C511E | 1-0102-PPID-C505 | Lubricated Plug | V422 | 75 | NG | Natural Gas
AREA Y - YARD / ELECTRICAL SUBSTATION
AREA B - SERVICE BUILDING
AREA M - ADMINISTRATION BUILDING
General Notes:
1. This schedule is provided for the Contractor's convenience and shall not be taken as complete.
2. Valves to be supplied and installed under this contract unless otherwise indicated.
3. n/a = not applicable; valve supplied by others, installed under this contract.
4. Refer to the scope of pre-purchased equipment for valves that are supplied by others to be installed under this contract.
Bottom of print range

## Motorized
SEWPCC UPGRADING/EXPANSION PROJECT
Electric Motor Actuated Valve Schedule
Location / Description | Tag Number | P&ID Number | Valve Type | Valve Type Number | Size (mm) | Commodity Code | Commodity | Maximum DP (kPa) | Maximum Flow (L/s) | Service [Note 1] | NEMA 250 Type | Voltage/ Phase | Travel Time (sec) | Control Features [Note 2] | Remarks
PROCESS MECHANICAL
AREA G - HEADWORKS
Raw Sewage Pumping
Raw Sewage Pump P-G101 Recycle Inlet | XV-G1062 | 1-0102-PPID-G101 | Knife gate | V150 | 300 | RS | Raw Sewage |  |  | O/C | 6 | 600/3 | ≤ 60 | C,D,H
Flushing Water to Raw Sewage Pump P-G101 Recycle | XV-G1063 | 1-0102-PPID-G101 | Ball | V308 | 50 | FSW | Flushing Water |  |  | O/C | 6 | 120/1 | ≤ 30 | C,E
Raw Sewage Pump P-G102 Inlet | XV-G1221 | 1-0102-PPID-G103 | Knife gate | V155 | 900 | RS | Raw Sewage | 60 | 1435 | O/C | 6 | 600/3 | ≤ 120 | C,D,I
Screening
Screenings to Washer/Compactor WCP-G231 | XV-G2311 | 1-0102-PPID-G203 | Knife gate | V150 | 400 | SCS | Screenings |  | 18.9 | O/C | 7 | 600/3 | ≤ 60 | C,D,H | Supplied by screening equipment vendor including remote control station.
Screenings to Washer/Compactor WCP-G232 | XV-G2321 | 1-0102-PPID-G203 | Knife gate | V150 | 400 | SCS | Screenings |  | 18.9 | O/C | 7 | 600/3 | ≤ 60 | C,D,H | Supplied by screening equipment vendor including remote control station.
Screenings Sluice Isolation Valve | XV-G2301 | 1-0102-PPID-G203 | Gate | V138 | 400 | SCS | Screenings |  | 18.9 | O/C | 7 | 600/3 | ≤ 60 | C,D | Provide actuator with intumescent coating for fire protection. Provide remote control station.
Grit Removal
Flushing Water to Grit Tank 1 | XV-G3211 | 1-0102-PPID-G301 | Ball | V308 | 25 | FSW | Flushing Water |  | 1.3 | O/C | 4X | 120/1 | ≤ 30 | C,E
Flushing Water to Grit Tank 2 | XV-G3221 | 1-0102-PPID-G301 | Ball | V308 | 25 | FSW | Flushing Water |  | 1.3 | O/C | 4X | 120/1 | ≤ 30 | C,E
Grit Slurry Pumps Suction Cross-connection | XV-G3236 | 1-0102-PPID-G302 | Knife gate | V150 | 100 | GRS | Grit Slurry |  | 18.9 | O/C | 4X | 600/3 | ≤ 30 | C,D,H
Grit Slurry Pumps Suction Cross-connection | XV-G3256 | 1-0102-PPID-G302 | Knife gate | V150 | 100 | GRS | Grit Slurry |  | 18.9 | O/C | 4X | 600/3 | ≤ 30 | C,D,H
Grit Slurry Pumps Discharge Cross-connection | XV-G3237 | 1-0102-PPID-G302 | Knife gate | V150 | 100 | GRS | Grit Slurry |  | 18.9 | O/C | 4X | 600/3 | ≤ 30 | C,D,H | Provide remote control station.
Grit Slurry Pumps Discharge Cross-connection | XV-G3257 | 1-0102-PPID-G302 | Knife gate | V150 | 100 | GRS | Grit Slurry |  | 18.9 | O/C | 4X | 600/3 | ≤ 30 | C,D,H | Provide remote control station.
Grit Cyclone CYC-G341-1 Inlet | XV-G3411 | 1-0102-PPID-G305 | Knife gate | V150 | 100 | GRS | Grit Slurry |  | 18.9 | O/C | 4X | 600/3 | ≤ 30 | C,D,H | Provide remote control station.
Grit Cyclone CYC-G341-2 Inlet | XV-G3412 | 1-0102-PPID-G305 | Knife gate | V150 | 100 | GRS | Grit Slurry |  | 18.9 | O/C | 4X | 600/3 | ≤ 30 | C,D,H | Provide remote control station.
Grit Cyclone CYC-G341-3 Inlet | XV-G3413 | 1-0102-PPID-G305 | Knife gate | V150 | 100 | GRS | Grit Slurry |  | 18.9 | O/C | 4X | 600/3 | ≤ 30 | C,D,H | Provide remote control station.
Grit Cyclone CYC-G342-1 Inlet | XV-G3421 | 1-0102-PPID-G305 | Knife gate | V150 | 100 | GRS | Grit Slurry |  | 18.9 | O/C | 4X | 600/3 | ≤ 30 | C,D,H | Provide remote control station.
Grit Cyclone CYC-G342-2 Inlet | XV-G3422 | 1-0102-PPID-G305 | Knife gate | V150 | 100 | GRS | Grit Slurry |  | 18.9 | O/C | 4X | 600/3 | ≤ 30 | C,D,H | Provide remote control station.
Grit Cyclone CYC-G342-3 Inlet | XV-G3423 | 1-0102-PPID-G305 | Knife gate | V150 | 100 | GRS | Grit Slurry |  | 18.9 | O/C | 4X | 600/3 | ≤ 30 | C,D,H | Provide remote control station.
Wash Water
Wash Water to Screen SCR-G211 | XV-G2112 | 1-0102-PPID-G201 | Ball | V308 | 38 | FSW | Flushing Water |  | 2.5 | O/C | 7 | 120/1 | ≤ 30 | J | Supplied by screen vendor.
Wash Water to Screen SCR-G212 | XV-G2122 | 1-0102-PPID-G201 | Ball | V308 | 38 | FSW | Flushing Water |  | 2.5 | O/C | 7 | 120/1 | ≤ 30 | J | Supplied by screen vendor.
Wash Water to Screen SCR-G213 | XV-G2132 | 1-0102-PPID-G202 | Ball | V308 | 38 | FSW | Flushing Water |  | 2.5 | O/C | 7 | 120/1 | ≤ 30 | J | Supplied by screen vendor.
Wash Water to Screen SCR-G214 | XV-G2142 | 1-0102-PPID-G202 | Ball | V308 | 38 | FSW | Flushing Water |  | 2.5 | O/C | 7 | 120/1 | ≤ 30 | J | Supplied by screen vendor.
Wash Water to Screen SCR-G211 | XV-G5341 | 1-0102-PPID-G508 | Three-way ball | V321 | 38 | FSW | Flushing Water |  | 2.5 | O/C | 4X | 120/1 | ≤ 30 | C,E
Wash Water to Screen SCR-G212 | XV-G5342 | 1-0102-PPID-G508 | Three-way ball | V321 | 38 | FSW | Flushing Water |  | 2.5 | O/C | 4X | 120/1 | ≤ 30 | C,E
Wash Water to Screen SCR-G213 | XV-G5343 | 1-0102-PPID-G508 | Three-way ball | V321 | 38 | FSW | Flushing Water |  | 2.5 | O/C | 4X | 120/1 | ≤ 30 | C,E
Wash Water to Screen SCR-G214 | XV-G5344 | 1-0102-PPID-G508 | Three-way ball | V321 | 38 | FSW | Flushing Water |  | 2.5 | O/C | 4X | 120/1 | ≤ 30 | C,E
Wash Water to Grit Classifier GRP-G341 | XV-G3414 | 1-0102-PPID-G305 | Ball | V308 | 25 | FSW | Flushing Water |  | 1 | O/C | 4X | 120/1 | ≤ 30 | C,E
Wash Water to Grit Classifier GRP-G342 | XV-G3424 | 1-0102-PPID-G305 | Ball | V308 | 25 | FSW | Flushing Water |  | 1 | O/C | 4X | 120/1 | ≤ 30 | C,E
Non-Potable Water (backup) for Wash Water | XV-G5345 | 1-0102-PPID-G508 | Ball | V308 | 38 | NPW | Non-Potable Water |  | 2.5 | O/C | 4X | 120/1 | ≤ 30 | C,E
Non-Potable Water (backup) for Wash Water | XV-G2303 | 1-0102-PPID-G203 | Ball | V308 | 25 | NPW | Non-Potable Water |  |  | O/C | 4X | 120/1 | ≤ 30 | C,E
Non-Potable Water (backup) for Wash Water | XV-G3401 | 1-0102-PPID-G305 | Ball | V308 | 25 | NPW | Non-Potable Water |  |  | O/C | 4X | 120/1 | ≤ 30 | C,E
Automatic Strainer STR-G535 Backwash Outlet | XV-G5351 | 1-0102-PPID-G508 | Ball | V308 | 25 | FSW | Flushing Water |  |  | O/C | 4X | 120/1 | ≤ 30 | J | Supplied by automatic strainer vendor.
Automatic Strainer STR-G536 Backwash Outlet | XV-G5361 | 1-0102-PPID-G508 | Ball | V308 | 25 | FSW | Flushing Water |  |  | O/C | 4X | 120/1 | ≤ 30 | J | Supplied by automatic strainer vendor.
Channel Aeration
Air Low Pressure to Grit Tanks 3 & 4 Effluent Channel | XV-G3312 | 1-0102-PPID-G303 | Butterfly | V510 | 150 | ALP | Air, Low Pressure |  |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H
Air Low Pressure to Grit Tanks 3 & 4 Influent Channel | XV-G3322 | 1-0102-PPID-G303 | Butterfly | V510 | 100 | ALP | Air, Low Pressure |  |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H
AREA P - PRIMARY CLARIFIERS
AREA R - BIOREACTORS / BLOWER BUILDING
Bioreactor 1
Primary Effluent to Pre-anoxic Zone Inlet | FV-R1011 | 1-0102-PPID-R101 | Butterfly | V500 | 350 | PE | Primary Effluent |  |  | M | 4X | 600/3 | ≤ 60 | C,D,G,H
RAS to Pre-anoxic Zone Inlet | LV-R1014 | 1-0102-PPID-R101 | Butterfly | V500 | 600 | RAS | Return Activated Sludge |  |  | M | 4X | 600/3 | ≤ 60 | C,D,G,H
Fermented Sludge Filtrate to Anaerobic Zone Inlet | FV-R1013 | 1-0102-PPID-R101 | Eccentric plug | V405 | 100 | FSF | Fermented Sludge Filtrate |  |  | M | 4X | 600/3 | ≤ 30 | C,D,G,H
Fermented Sludge Filtrate to Anoxic Zone Inlet | FV-R1023 | 1-0102-PPID-R101 | Eccentric plug | V405 | 75 | FSF | Fermented Sludge Filtrate |  |  | M | 4X | 600/3 | ≤ 30 | C,D,G,H
Primary Effluent to Anaerobic Zone Inlet | LV-R1024 | 1-0102-PPID-R101 | Rectang. Butterfly valve | V515 | 711 x 2372 | PE | Primary Effluent |  |  | M | 4X | 600/3 | ≤ 60 | C,D,G,H | Rectangular butterfly gate. See drawings for details.
Primary Effluent to Anoxic Zone Inlet | LV-R1034 | 1-0102-PPID-R101 | Rectang. Butterfly valve | V515 | 711 x 2372 | PE | Primary Effluent |  |  | M | 4X | 600/3 | ≤ 60 | C,D,G,H | Rectangular butterfly gate. See drawings for details.
Flushing Service Water to Spray Nozzles | XV-R1049 | 1-0102-PPID-R102 | Eccentric plug | V405 | 75 | FSW | Flushing Water |  |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H
Air Low Pressure to IFAS Distribution Channel | XV-R1046 | 1-0102-PPID-R102 | Butterfly | V514 | 100 | ALP | Air, Low Pressure |  |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H | Set valve opening limit to 25%
Air Low Pressure to IFAS Zone | FV-R1047 | 1-0102-PPID-R102 | Butterfly | V514 | 400 | ALP | Air, Low Pressure |  |  | M | 4X | 600/3 | ≤ 30 | C,D,G,H | Provide remote control station
Air Low Pressure to IFAS Media Screens | XV-R1048 | 1-0102-PPID-R102 | Butterfly | V514 | 75 | ALP | Air, Low Pressure |  |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H | Set valve opening limit to 25%
Air Low Pressure to Post Aerobic Zone | FV-R1056 | 1-0102-PPID-R102 | Butterfly | V514 | 100 | ALP | Air, Low Pressure |  |  | M | 4X | 600/3 | ≤ 30 | C,D,G,H | Provide remote control station
Air Low Pressure to Post Aerobic Zone | FV-R1057 | 1-0102-PPID-R102 | Butterfly | V514 | 100 | ALP | Air, Low Pressure |  |  | M | 4X | 600/3 | ≤ 30 | C,D,G,H | Provide remote control station
Bioreactor 2
Primary Effluent to Pre-anoxic Zone Inlet | FV-R1111 | 1-0102-PPID-R103 | Butterfly | V500 | 350 | PE | Primary Effluent |  |  | M | 4X | 600/3 | ≤ 60 | C,D,G,H
RAS to Pre-anoxic Zone Inlet | LV-R1114 | 1-0102-PPID-R103 | Butterfly | V500 | 600 | RAS | Return Activated Sludge |  |  | M | 4X | 600/3 | ≤ 60 | C,D,G,H
Fermented Sludge Filtrate to Anaerobic Zone Inlet | FV-R1113 | 1-0102-PPID-R103 | Eccentric plug | V405 | 100 | FSF | Fermented Sludge Filtrate |  |  | M | 4X | 600/3 | ≤ 30 | C,D,G,H
Fermented Sludge Filtrate to Anoxic Zone Inlet | FV-R1123 | 1-0102-PPID-R103 | Eccentric plug | V405 | 75 | FSF | Fermented Sludge Filtrate |  |  | M | 4X | 600/3 | ≤ 30 | C,D,G,H
Primary Effluent to Anaerobic Zone Inlet | LV-R1124 | 1-0102-PPID-R103 | Rectang. Butterfly valve | V515 | 711 x 2372 | PE | Primary Effluent |  |  | M | 4X | 600/3 | ≤ 60 | C,D,G,H | Rectangular butterfly gate. See drawings for details.
Primary Effluent to Anoxic Zone Inlet | LV-R1134 | 1-0102-PPID-R103 | Rectang. Butterfly valve | V515 | 711 x 2372 | PE | Primary Effluent |  |  | M | 4X | 600/3 | ≤ 60 | C,D,G,H | Rectangular butterfly gate. See drawings for details.
Flushing Service Water to Spray Nozzles | XV-R1149 | 1-0102-PPID-R104 | Eccentric plug | V405 | 75 | FSW | Flushing Water |  |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H
Air Low Pressure to IFAS Distribution Channel | XV-R1146 | 1-0102-PPID-R104 | Butterfly | V514 | 100 | ALP | Air, Low Pressure |  |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H | Set valve opening limit to 25%
Air Low Pressure to IFAS Zone | FV-R1147 | 1-0102-PPID-R104 | Butterfly | V514 | 400 | ALP | Air, Low Pressure |  |  | M | 4X | 600/3 | ≤ 30 | C,D,G,H | Provide remote control station
Air Low Pressure to IFAS Media Screens | XV-R1148 | 1-0102-PPID-R104 | Butterfly | V514 | 75 | ALP | Air, Low Pressure |  |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H | Set valve opening limit to 25%
Air Low Pressure to Post Aerobic Zone | FV-R1156 | 1-0102-PPID-R104 | Butterfly | V514 | 100 | ALP | Air, Low Pressure |  |  | M | 4X | 600/3 | ≤ 30 | C,D,G,H | Provide remote control station
Air Low Pressure to Post Aerobic Zone | FV-R1157 | 1-0102-PPID-R104 | Butterfly | V514 | 100 | ALP | Air, Low Pressure |  |  | M | 4X | 600/3 | ≤ 30 | C,D,G,H | Provide remote control station
Bioreactor 3
Primary Effluent to Pre-anoxic Zone Inlet | FV-R1211 | 1-0102-PPID-R105 | Butterfly | V500 | 350 | PE | Primary Effluent |  |  | M | 4X | 600/3 | ≤ 60 | C,D,G,H
RAS to Pre-anoxic Zone Inlet | LV-R1214 | 1-0102-PPID-R105 | Butterfly | V500 | 600 | RAS | Return Activated Sludge |  |  | M | 4X | 600/3 | ≤ 60 | C,D,G,H
Fermented Sludge Filtrate to Anaerobic Zone Inlet | FV-R1213 | 1-0102-PPID-R105 | Eccentric plug | V405 | 100 | FSF | Fermented Sludge Filtrate |  |  | M | 4X | 600/3 | ≤ 30 | C,D,G,H
Fermented Sludge Filtrate to Anoxic Zone Inlet | FV-R1223 | 1-0102-PPID-R105 | Eccentric plug | V405 | 75 | FSF | Fermented Sludge Filtrate |  |  | M | 4X | 600/3 | ≤ 30 | C,D,G,H
Primary Effluent to Anaerobic Zone Inlet | LV-R1224 | 1-0102-PPID-R105 | Rectang. Butterfly valve | V515 | 711 x 2372 | PE | Primary Effluent |  |  | M | 4X | 600/3 | ≤ 60 | C,D,G,H | Rectangular butterfly gate. See drawings for details.
Primary Effluent to Anoxic Zone Inlet | LV-R1234 | 1-0102-PPID-R105 | Rectang. Butterfly valve | V515 | 711 x 2372 | PE | Primary Effluent |  |  | M | 4X | 600/3 | ≤ 60 | C,D,G,H | Rectangular butterfly gate. See drawings for details.
Flushing Service Water to Spray Nozzles | XV-R1249 | 1-0102-PPID-R106 | Eccentric plug | V405 | 75 | FSW | Flushing Water |  |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H
Air Low Pressure to IFAS Distribution Channel | XV-R1246 | 1-0102-PPID-R106 | Butterfly | V514 | 100 | ALP | Air, Low Pressure |  |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H | Set valve opening limit to 25%
Air Low Pressure to IFAS Zone | FV-R1247 | 1-0102-PPID-R106 | Butterfly | V514 | 400 | ALP | Air, Low Pressure |  |  | M | 4X | 600/3 | ≤ 30 | C,D,G,H | Provide remote control station
Air Low Pressure to IFAS Media Screens | XV-R1248 | 1-0102-PPID-R106 | Butterfly | V514 | 75 | ALP | Air, Low Pressure |  |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H | Set valve opening limit to 25%
Air Low Pressure to Post Aerobic Zone | FV-R1256 | 1-0102-PPID-R106 | Butterfly | V514 | 100 | ALP | Air, Low Pressure |  |  | M | 4X | 600/3 | ≤ 30 | C,D,G,H | Provide remote control station
Air Low Pressure to Post Aerobic Zone | FV-R1257 | 1-0102-PPID-R106 | Butterfly | V514 | 100 | ALP | Air, Low Pressure |  |  | M | 4X | 600/3 | ≤ 30 | C,D,G,H | Provide remote control station
Miscelleaneous
WAS RDT Feed Pumps Discharge Cross-connection | XV-R3013 | 1-0102-PPID-R301 | Eccentric plug | V405 | 150 | WAS | Waste Activated Sludge |  |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H
WAS RDT Feed Pumps Discharge Cross-connection | XV-R3033 | 1-0102-PPID-R301 | Eccentric plug | V405 | 150 | WAS | Waste Activated Sludge |  |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H
WAS Mixing Pump P-R304 Outlet to Scum Nozzle | XV-R3041 | 1-0102-PPID-R301 | Eccentric plug | V405 | 150 | WAS | Waste Activated Sludge |  |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H
Blower Building
Blower B-R201 Blowoff Outlet | XV-R2015 | 1-0102-PPID-R201 | N/A | N/A | N/A | ALP | Air, Low Pressure |  |  | O/C | 4X |  |  | J | Supplied by blower vendor.
Blower B-R202 Blowoff Outlet | XV-R2025 | 1-0102-PPID-R201 | N/A | N/A | N/A | ALP | Air, Low Pressure |  |  | O/C | 4X |  |  | J | Supplied by blower vendor.
Blower B-R203 Blowoff Outlet | XV-R2035 | 1-0102-PPID-R202 | N/A | N/A | N/A | ALP | Air, Low Pressure |  |  | O/C | 4X |  |  | J | Supplied by blower vendor.
Blower B-R204 Blowoff Outlet | XV-R2045 | 1-0102-PPID-R202 | N/A | N/A | N/A | ALP | Air, Low Pressure |  |  | O/C | 4X |  |  | J | Supplied by blower vendor.
Blower B-R205 Blowoff Outlet | XV-R2055 | 1-0102-PPID-R203 | N/A | N/A | N/A | ALP | Air, Low Pressure |  |  | O/C | 4X |  |  | J | Supplied by blower vendor.
Blower B-R206 Blowoff Outlet | XV-R2065 | 1-0102-PPID-R203 | N/A | N/A | N/A | ALP | Air, Low Pressure |  |  | O/C | 4X |  |  | J | Supplied by blower vendor.
Air Low Pressure to Hoar Frost | XV-R2001 | 1-0102-PPID-R201 | Butterfly | V514 | 150 | ALP | Air, Low Pressure |  |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H
Air Low Pressure to PE Channel | XV-R2201 | 1-0102-PPID-R102 | Butterfly | V514 | 150 | ALP | Air, Low Pressure |  |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H | Set valve opening limit to 25%
Air Low Pressure to RAS Channel | XV-R2202 | 1-0102-PPID-R102 | Butterfly | V514 | 150 | ALP | Air, Low Pressure |  |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H | Set valve opening limit to 25%
Air Low Pressure to Mixed Liquor Channel | XV-R1305 | 1-0102-PPID-R107 | Butterfly | V514 | 150 | ALP | Air, Low Pressure |  |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H | Set valve opening limit to 25%
AREA S - SECONDARY CLARIFIERS
Clarifier 4 ML Inlet | FV-S1421 | 1-0102-PPID-S105 | Butterfly | V500 | 900 | ML | Mixed Liquor |  | 1100 | M | 4X | 600/3 | ≤ 60 | C,D,G,H
Clarifier 5 ML Inlet | FV-S1521 | 1-0102-PPID-S106 | Butterfly | V500 | 900 | ML | Mixed Liquor |  | 1100 | M | 4X | 600/3 | ≤ 60 | C,D,G,H
Sludge transfer pump P-S401 outlet | XV-S4013 | 1-0102-PPID-S208 | Ball | V315 | 200 | STS | Southend Thickened Sludge | 400 | 8.3 | O/C | 4X | 600/3 | ≤ 30 | C,D,H
Sludge transfer pump P-S402 outlet | XV-S4023 | 1-0102-PPID-S208 | Ball | V315 | 200 | STS | Southend Thickened Sludge | 400 | 8.3 | O/C | 4X | 600/3 | ≤ 30 | C,D,H
Flushing water for scum pumps P-S316 and P-S317 | XV-S3162 | 1-0102-PPID-S303 | Ball | V315 | 38 | FSW | Flushing Water | 800 | 3.2 | O/C | 4X | 120/1 | ≤ 30 | C,E
Scum pumps P-S316 and P-S317 recirculation | XV-S3163 | 1-0102-PPID-S303 | Ball | V315 | 100 | SC | Scum | 200 | 10 | O/C | 4X | 600/3 | ≤ 30 | C,D,H | Provide remote control station
Scum pumps P-S316 and P-S317 Outlet | XV-S3172 | 1-0102-PPID-S303 | Ball | V315 | 100 | SC | Scum | 200 | 10 | O/C | 4X | 600/3 | ≤ 30 | C,D,H | Provide remote control station
Scum header | XV-S3002 | 1-0102-PPID-S304 | Ball | V315 | 150 | SC | Scum | 150 |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H | Provide remote control station
Scum piping between new 150 pipe and exist. 100 pipe | XV-S3001 | 1-0102-PPID-S304 | Ball | V315 | 100 | SC | Scum | 150 |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H | Provide remote control station
Instrument Air Supply | XV-S5408 | 1-0102-PPID-S107 | [11 empty] | J | Supplied by Package Sampler Vendor
AREA U - UV DISINFECTION BUILDING
AREA K - HIGH RATE CLARIFIERS
Flushing Water to HRC Influent Channel 1 | XV-G3622 | 1-0102-PPID-K101 | Butterfly | V500 | 100 | FSW | Flushing Water |  |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H
Flushing Water to HRC Influent Channel 2 | XV-G3632 | 1-0102-PPID-K101 | Butterfly | V500 | 100 | FSW | Flushing Water |  |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H
Sodium Hypochlorite to HRC Train 1 Inlet | XV-K1103 | 1-0102-PPID-K102 | Ball | V330 | 38 | SHC | Sodium Hypochlorite |  |  | O/C | 7 | 120/1 | ≤ 30 | C,E
Sodium Hypochlorite to HRC Train 2 Inlet | XV-K1203 | 1-0102-PPID-K104 | Ball | V330 | 38 | SHC | Sodium Hypochlorite |  |  | O/C | 7 | 120/1 | ≤ 30 | C,E
Sodium Hypochlorite to HRC Train 1 Maturation Tank | XV-K1134 | 1-0102-PPID-K103 | Ball | V330 | 38 | SHC | Sodium Hypochlorite |  |  | O/C | 7 | 120/1 | ≤ 30 | C,E
Sodium Hypochlorite to HRC Train 2 Maturation Tank | XV-K1234 | 1-0102-PPID-K105 | Ball | V330 | 38 | SHC | Sodium Hypochlorite |  |  | O/C | 7 | 120/1 | ≤ 30 | C,E
Drain from HRC Train 1 Maturation Tank | XY-K1131 | 1-0102-PPID-K103 | Mud | V915 | 150 | PD | Process Drain |  |  | O/C | 7 | 600/3 | ≤ 30 | C,D,H
Drain from HRC Train 2 Maturation Tank | XY-K1231 | 1-0102-PPID-K105 | Mud | V915 | 150 | PD | Process Drain |  |  | O/C | 7 | 600/3 | ≤ 30 | C,D,H
HRC Train 1 Lamella Drain | XV-K1145 | 1-0102-PPID-K103 | Eccentric plug | V405 | 150 | PD | Process Drain |  |  | T | 4X | 600/3 | ≤ 30 | C,D,H
HRC Train 2 Lamella Drain | XV-K1245 | 1-0102-PPID-K105 | Eccentric plug | V405 | 150 | PD | Process Drain |  |  | T | 4X | 600/3 | ≤ 30 | C,D,H
Flushing Water to HRC Effluent Drop Shaft Spray Nozzle | XV-K1512 | 1-0102-PPID-K106 | Ball | V308 | 12 | FSW | Flushing Water |  |  | O/C | 4X | 120/1 | ≤ 30 | C,E
HRC Train 1 Effluent Sample Line Inlet | XV-K1155 | 1-0102-PPID-K106 | Ball | V330 | 25 | SAM | Sample |  |  | O/C | 4X | 120/1 | ≤ 30 | C,E
HRC Train 2 Effluent Sample Line Inlet | XV-K1255 | 1-0102-PPID-K106 | Ball | V330 | 25 | SAM | Sample |  |  | O/C | 4X | 120/1 | ≤ 30 | C,E
Polymer to HRC Train 1 Cyclone K211 Underflow | XV-K1123 | 1-0102-PPID-K107 | Ball | V330 | 25 | MP | Mixed Polymer |  |  | O/C | 7 | 120/1 | ≤ 30 | C,E
Polymer to HRC Train 1 Cyclone K212 Underflow | XV-K1124 | 1-0102-PPID-K107 | Ball | V330 | 25 | MP | Mixed Polymer |  |  | O/C | 7 | 120/1 | ≤ 30 | C,E
Polymer to HRC Train 1 Cyclone K213 Underflow | XV-K1125 | 1-0102-PPID-K107 | Ball | V330 | 25 | MP | Mixed Polymer |  |  | O/C | 7 | 120/1 | ≤ 30 | C,E
Polymer to HRC Train 2 Cyclone K221 Underflow | XV-K1223 | 1-0102-PPID-K107 | Ball | V330 | 25 | MP | Mixed Polymer |  |  | O/C | 7 | 120/1 | ≤ 30 | C,E
Polymer to HRC Train 2 Cyclone K222 Underflow | XV-K1224 | 1-0102-PPID-K107 | Ball | V330 | 25 | MP | Mixed Polymer |  |  | O/C | 7 | 120/1 | ≤ 30 | C,E
Polymer to HRC Train 2 Cyclone K223 Underflow | XV-K1225 | 1-0102-PPID-K107 | Ball | V330 | 25 | MP | Mixed Polymer |  |  | O/C | 7 | 120/1 | ≤ 30 | C,E
HRS to Primary Influent Channel | XV-K2543 | 1-0102-PPID-K203 | Eccentric plug | V405 | 300 | HRS | High Rate Clarifier Sludge |  |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H
HRS to Fermenters Cell No. 4 | XV-K2544 | 1-0102-PPID-K203 | Eccentric plug | V405 | 300 | HRS | High Rate Clarifier Sludge |  |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H
Sand Slurry to HRC Train 1 Injection Zone | XV-K1121 | 1-0102-PPID-K301 | Eccentric plug | V405 | 50 | SNS | Sand Slurry |  |  | - | - | 600/3 | - | C,D,H | Supplied by HRC vendor
Sand Slurry to HRC Train 2 Injection Zone | XV-K1221 | 1-0102-PPID-K301 | Eccentric plug | V405 | 50 | SNS | Sand Slurry |  |  | - | - | 600/3 | - | C,D,H | Supplied by HRC vendor
AREA D - FERMENTERS / THICKENERS
Fermenters
Flushing Water to PS Fermenters Train 1 Cell 1 | FV-D3013 | 1-0102-PPID-D301 | Ball | V308 | 75 | FSW | Flushing Water |  |  | M | 7 | 600/3 | ≤ 30 | C,D,G,H
Flushing Water to PS Fermenters Train 1 Cell 1 | XV-D3012 | 1-0102-PPID-D301 | Ball | V308 | 75 | FSW | Flushing Water |  |  | O/C | 7 | 600/3 | ≤ 30 | C,D,H
Flushing Water to PS Fermenters Train 1 Cell 2 | XV-D3022 | 1-0102-PPID-D301 | Ball | V308 | 75 | FSW | Flushing Water |  |  | O/C | 7 | 600/3 | ≤ 30 | C,D,H
Flushing Water to PS Fermenters Train 1 Cell 3 | XV-D3032 | 1-0102-PPID-D301 | Ball | V308 | 75 | FSW | Flushing Water |  |  | O/C | 7 | 600/3 | ≤ 30 | C,D,H
Primary Sludge to PS Fermenters Train 1 Cell 1 | XV-D3011 | 1-0102-PPID-D301 | Eccentric plug | V405 | 150 | PS | Primary Sludge |  |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H | Provide remote control station
Primary Sludge to PS Fermenters Train 1 Cell 4 | XV-D3043 | 1-0102-PPID-D301 | Eccentric plug | V405 | 150 | PS | Primary Sludge |  |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H
Flushing Water to PS Fermenters Train 1 Cell 4 | XV-D3048 | 1-0102-PPID-D301 | Ball | V315 | 75 | FSW | Flushing Water |  |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H
Flushing Water to PS Fermenters Train 1 Cell 4 | XV-D3049 | 1-0102-PPID-D301 | Ball | V315 | 75 | FSW | Flushing Water |  |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H
Flushing Water to PS Fermenters Train 2 Cell 1 | FV-D3113 | 1-0102-PPID-D302 | Ball | V308 | 75 | FSW | Flushing Water |  |  | M | 7 | 600/3 | ≤ 30 | C,D,G,H
Flushing Water to PS Fermenters Train 2 Cell 1 | XV-D3112 | 1-0102-PPID-D302 | Ball | V308 | 75 | FSW | Flushing Water |  |  | O/C | 7 | 600/3 | ≤ 30 | C,D,H
Flushing Water to PS Fermenters Train 2 Cell 2 | XV-D3122 | 1-0102-PPID-D302 | Ball | V308 | 75 | FSW | Flushing Water |  |  | O/C | 7 | 600/3 | ≤ 30 | C,D,H
Flushing Water to PS Fermenters Train 2 Cell 3 | XV-D3132 | 1-0102-PPID-D302 | Ball | V308 | 75 | FSW | Flushing Water |  |  | O/C | 7 | 600/3 | ≤ 30 | C,D,H
Primary Sludge to PS Fermenters Train 2 Cell 1 | XV-D3111 | 1-0102-PPID-D302 | Eccentric plug | V405 | 150 | PS | Primary Sludge |  |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H | Provide remote control station
Primary Sludge to PS Fermenters Train 2 Cell 4 | XV-D3143 | 1-0102-PPID-D302 | Eccentric plug | V405 | 150 | PS | Primary Sludge |  |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H
Flushing Water to PS Fermenters Train 2 Cell 4 | XV-D3148 | 1-0102-PPID-D302 | Ball | V315 | 75 | FSW | Flushing Water |  |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H
Flushing Water to PS Fermenters Train 2 Cell 4 | XV-D3149 | 1-0102-PPID-D302 | Ball | V315 | 75 | FSW | Flushing Water |  |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H
Thickeners
WAS RDT RDT-D403 Inlet | XV-D4031 | 1-0102-PPID-D402 | Eccentric plug | V405 | 150 | WAS | Waste Activated Sludge |  |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H
WAS RDT RDT-D404 Inlet | XV-D4041 | 1-0102-PPID-D402 | Eccentric plug | V405 | 150 | WAS | Waste Activated Sludge |  |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H
Flushing Water to WAS RDT RDT-D403 Inlet Piping | XV-D4032 | 1-0102-PPID-D402 | Ball | V308 | 38 | FSW | Flushing Water |  |  | O/C | 4X | 120/1 | ≤ 30 | C,E
Flushing Water to WAS RDT RDT-D404 Inlet Piping | XV-D4042 | 1-0102-PPID-D402 | Ball | V308 | 38 | FSW | Flushing Water |  |  | O/C | 4X | 120/1 | ≤ 30 | C,E
Flushing Water to WAS RDT RDT-D403 | XV-D4034 | 1-0102-PPID-D402 | Ball | V308 | 38 | FSW | Flushing Water |  |  | O/C | 4X | 120/1 | ≤ 30 | J | Supplied by RDT vendor
Flushing Water to WAS RDT RDT-D404 | XV-D4044 | 1-0102-PPID-D402 | Ball | V308 | 38 | FSW | Flushing Water |  |  | O/C | 4X | 120/1 | ≤ 30 | J | Supplied by RDT vendor
FSL RDT Feed Pumps Discharge Cross-connection | XV-D4113 | 1-0102-PPID-D404 | Eccentric plug | V405 | 150 | FSL | Fermented Sludge |  |  | O/C | 4X | 600/3 | ≤ 30 | C,E
FSL RDT Feed Pumps Discharge Cross-connection | XV-D4123 | 1-0102-PPID-D404 | Eccentric plug | V405 | 150 | FSL | Fermented Sludge |  |  | O/C | 4X | 600/3 | ≤ 30 | C,E
FSL RDT Feed Pumps Discharge Cross-connection | XV-D4133 | 1-0102-PPID-D405 | Eccentric plug | V405 | 150 | FSL | Fermented Sludge |  |  | O/C | 4X | 600/3 | ≤ 30 | C,E
FSL RDT RDT-D415 Inlet | XV-D4151 | 1-0102-PPID-D406 | Eccentric plug | V405 | 150 | FSL | Fermented Sludge |  |  | O/C | 4X | 600/3 | ≤ 30 | C,E
FSL RDT RDT-D416 Inlet | XV-D4161 | 1-0102-PPID-D406 | Eccentric plug | V405 | 150 | FSL | Fermented Sludge |  |  | O/C | 4X | 600/3 | ≤ 30 | C,E
FSL RDT RDT-D417 Inlet | XV-D4171 | 1-0102-PPID-D407 | Eccentric plug | V405 | 150 | FSL | Fermented Sludge |  |  | O/C | 4X | 600/3 | ≤ 30 | C,E
Flushing Water to FSL RDT RDT-D415 Inlet Piping | XV-D4152 | 1-0102-PPID-D406 | Ball | V308 | 38 | FSW | Flushing Water |  |  | O/C | 4X | 120/1 | ≤ 30 | C,E
Flushing Water to FSL RDT RDT-D416 Inlet Piping | XV-D4162 | 1-0102-PPID-D406 | Ball | V308 | 38 | FSW | Flushing Water |  |  | O/C | 4X | 120/1 | ≤ 30 | C,E
Flushing Water to FSL RDT RDT-D417 Inlet Piping | XV-D4172 | 1-0102-PPID-D407 | Ball | V308 | 38 | FSW | Flushing Water |  |  | O/C | 4X | 120/1 | ≤ 30 | C,E
Flushing Water to FSL RDT RDT-D415 | XV-D4154 | 1-0102-PPID-D406 | Ball | V308 | 38 | FSW | Flushing Water |  |  | O/C | 4X | 120/1 | ≤ 30 | J | Supplied by RDT vendor
Flushing Water to FSL RDT RDT-D416 | XV-D4164 | 1-0102-PPID-D406 | Ball | V308 | 38 | FSW | Flushing Water |  |  | O/C | 4X | 120/1 | ≤ 30 | J | Supplied by RDT vendor
Flushing Water to FSL RDT RDT-D417 | XV-D4174 | 1-0102-PPID-D407 | Ball | V308 | 38 | FSW | Flushing Water |  |  | O/C | 4X | 120/1 | ≤ 30 | J | Supplied by RDT vendor
Automatic Strainer STR-D433 Backwash Outlet | XV-D4331 | 1-0102-PPID-D410 | Ball | V308 | 25 | PD | Process Drain |  |  | O/C | 4X | 120/1 | ≤ 30 | J | Supplied by automatic strainer vendor
Automatic Strainer STR-D434 Backwash Outlet | XV-D4341 | 1-0102-PPID-D410 | Ball | V308 | 25 | PD | Process Drain |  |  | O/C | 4X | 120/1 | ≤ 30 | J | Supplied by automatic strainer vendor
WAS Filtrate Pump P-D451 Outlet | LV-D4513 | 1-0102-PPID-D411 | Butterfly | V514 | 150 | WSF | Waste Activated Sludge Filtrate |  |  | M | 4X | 600/3 | ≤ 30 | C,D,G,H
WAS Filtrate Pump P-D452 Outlet | LV-D4523 | 1-0102-PPID-D411 | Butterfly | V514 | 150 | WSF | Waste Activated Sludge Filtrate |  |  | M | 4X | 600/3 | ≤ 30 | C,D,G,H
FSL Filtrate Pump P-D461 Outlet | LV-D4613 | 1-0102-PPID-D412 | Butterfly | V514 | 150 | FSF | Fermented Sludge Filtrate |  |  | M | 4X | 600/3 | ≤ 30 | C,D,G,H
FSL Filtrate Pump P-D462 Outlet | LV-D4623 | 1-0102-PPID-D412 | Butterfly | V514 | 150 | FSF | Fermented Sludge Filtrate |  |  | M | 4X | 600/3 | ≤ 30 | C,D,G,H
FSL Filtrate Pump P-D463 Outlet | LV-D4633 | 1-0102-PPID-D413 | Butterfly | V514 | 150 | FSF | Fermented Sludge Filtrate |  |  | M | 4X | 600/3 | ≤ 30 | C,D,G,H
FSL Filtrate Pump P-D464 Outlet | LV-D4643 | 1-0102-PPID-D413 | Butterfly | V514 | 150 | FSF | Fermented Sludge Filtrate |  |  | M | 4X | 600/3 | ≤ 30 | C,D,G,H
AREA T - BIOFILTER / ODOUR CONTROL
Glycol Recirculation | TV-T1042 | 1-0102-PPID-T102 | Threeway | - | 75 | GS | Glycol Supply |  |  | M | 7 | 600/3 | ≤ 30 | J | Supplied by Biofilter vendor, Expl. Proof. Class1 Div 2
Recirculation Pumps P-T111 and P-T112 | XV-T1109 | 1-0102-PPID-T104 | Ball | V330 | 25 | PD | Process Drain |  |  | O/C | 7 | 120/1 | ≤ 30 | J | Supplied by Biofilter vendor, Expl. Proof. Class1 Div 2
Recirculation Pumps P-T121 and P-T122 | XV-T1209 | 1-0102-PPID-T106 | Ball | V330 | 25 | PD | Process Drain |  |  | O/C | 7 | 120/1 | ≤ 30 | J | Supplied by Biofilter vendor, Expl. Proof. Class1 Div 2
Biofilter Microstrainer Blowdown | XV-T1401 | 1-0102-PPID-T107 | Ball | V330 | 25 | PD | Process Drain |  |  | O/C | 4X | 120/1 | ≤ 30 | J | Supplied by Microstrainer vendor.
Biofilter Microstrainer Outlet | XV-T1402 | 1-0102-PPID-T107 | Ball | V307 | 75 | FSW | Flushing Water |  |  | O/C | 4X | 600/3 | ≤ 30 | C,D,H
Non Potable Water Feed | XV-T1406 | 1-0102-PPID-T107 | Ball | V307 | 38 | NPW | Non-Potable Water |  |  | O/C | 4X | 120/1 | ≤ 30 | C,E
FSW Feed to Biofilter TK-T210 | XV-T2101 | 1-0102-PPID-T107 | Ball | V307 | 25 | FSW | Flushing Water |  |  | O/C | 7 | - | ≤ 30 | J | Supplied by Biofilter vendor, Expl. Proof. Class1 Div 2
FSW Feed to Biofilter TK-T220 | XV-T2201 | 1-0102-PPID-T107 | Ball | V307 | 25 | FSW | Flushing Water |  |  | O/C | 7 | - | ≤ 30 | J | Supplied by Biofilter vendor, Expl. Proof. Class1 Div 2
FSW Feed to Biofilter TK-T230 | XV-T2301 | 1-0102-PPID-T107 | Ball | V307 | 25 | FSW | Flushing Water |  |  | O/C | 7 | - | ≤ 30 | J | Supplied by Biofilter vendor, Expl. Proof. Class1 Div 2
Biofilter Exhaust Fan EF-T301 Inlet | XV-T3011 | 1-0102-PPID-T301 | Isolation Damper | V965 | 1200 | FOA | Foul Air |  |  | O/C | 8 | 600/3 | ≤ 30 | C,D,H | Explosion Proof, Class 1 Div 2
Biofilter Exhaust Fan EF-T302 Inlet | XV-T3021 | 1-0102-PPID-T301 | Isolation Damper | V965 | 1200 | FOA | Foul Air |  |  | O/C | 8 | 600/3 | ≤ 30 | C,D,H | Explosion Proof, Class 1 Div 2
AREA C - CHEMICAL BUILDING / ELECTRICAL BUILDING
Ferric Chloride System
Chemical fill line to TK-C101 isolation valve | XV-C1012 | 1-0102-PPID-C101 | Ball | V330 | 75 | FC | Ferric Chloride |  |  | O/C | 4X | 120/1 | < 60 | C,F | Electric actuator for chemical service
Chemical fill line to TK-C102 isolation valve | XV-C1022 | 1-0102-PPID-C101 | Ball | V330 | 75 | FC | Ferric Chloride |  |  | O/C | 4X | 120/1 | < 60 | C,F | Electric actuator for chemical service
Chemical fill line to TK-C103 isolation valve | XV-C1032 | 1-0102-PPID-C101 | Ball | V330 | 75 | FC | Ferric Chloride |  |  | O/C | 4X | 120/1 | < 60 | C,F | Electric actuator for chemical service
Tank TK-C101 outlet isolation valve | XV-C1013 | 1-0102-PPID-C101 | Ball | V330 | 50 | FC | Ferric Chloride |  | 0.55 | O/C | 4X | 120/1 | < 60 | C,F | Electric actuator for chemical service
Tank TK-C102 outlet isolation valve | XV-C1023 | 1-0102-PPID-C101 | Ball | V330 | 50 | FC | Ferric Chloride |  | 0.55 | O/C | 4X | 120/1 | < 60 | C,F | Electric actuator for chemical service
Tank TK-C103 outlet isolation valve | XV-C1033 | 1-0102-PPID-C101 | Ball | V330 | 50 | FC | Ferric Chloride |  | 0.55 | O/C | 4X | 120/1 | < 60 | C,F | Electric actuator for chemical service
Sodium Hypochlorite System
Chemical fill line to TK-C201 isolation valve | XV-C2012 | 1-0102-PPID-C201 | Ball | V330 | 75 | SHC | Sodium Hypochlorite |  |  | O/C | 4X | 120/1 | < 60 | C,F | Electric actuator for chemical service
Chemical fill line to TK-C202 isolation valve | XV-C2022 | 1-0102-PPID-C201 | Ball | V330 | 75 | SHC | Sodium Hypochlorite |  |  | O/C | 4X | 120/1 | < 60 | C,F | Electric actuator for chemical service
Tank TK-C201 outlet isolation valve | XV-C2013 | 1-0102-PPID-C201 | Ball | V330 | 50 | SHC | Sodium Hypochlorite |  | 0.52833 | O/C | 4X | 120/1 | < 60 | C,F | Electric actuator for chemical service
Tank TK-C202 outlet isolation valve | XV-C2023 | 1-0102-PPID-C201 | Ball | V330 | 50 | SHC | Sodium Hypochlorite |  | 0.52833 | O/C | 4X | 120/1 | < 60 | C,F | Electric actuator for chemical service
Sodium hypochlorite skid pump P-C222 isolation valve | XV-C2223 | 1-0102-PPID-C205 | Ball | V330 | 25 | SHC | Sodium Hypochlorite |  | 0.32667 | O/C | 4X | 120/1 | < 60 | C,F | Electric actuator for chemical service - by skid supplier
Sodium hypochlorite skid pump P-C222 isolation valve | XV-C2224 | 1-0102-PPID-C205 | Ball | V330 | 25 | SHC | Sodium Hypochlorite |  | 0.32667 | O/C | 4X | 120/1 | < 60 | C,F | Electric actuator for chemical service - by skid supplier
Sodium Hydroxide System
Chemical fill line to TK-C205 isolation valve | XV-C2052 | 1-0102-PPID-C201 | Ball | V330 | 75 | SHD | Sodium Hydroxide |  |  | O/C | 4X | 120/1 | < 60 | C,F | Electric actuator for chemical service
Tank TK-C205 outlet isolation valve | XV-C2053 | 1-0102-PPID-C201 | Ball | V330 | 50 | SHD | Sodium Hydroxide |  | 0.053333 | O/C | 4X | 120/1 | < 60 | C,F | Electric actuator for chemical service
Sodium Bisulphite System
Chemical fill line to TK-C301 isolation valve | XV-C3012 | 1-0102-PPID-C301 | Ball | V330 | 75 | SBS | Sodium Bisulphite |  |  | O/C | 4X | 120/1 | < 60 | C,F | Electric actuator for chemical service
Tank TK-C301 outlet isolation valve | XV-C3013 | 1-0102-PPID-C301 | Ball | V330 | 50 | SBS | Sodium Bisulphite |  | 0.11 | O/C | 4X | 120/1 | < 60 | C,F | Electric actuator for chemical service
Flushing Water | FV-C3104 | 1-0102-PPID-C301 | Ball | V307 | 50 | FSW | Flushing Water |  |  | O/C | 4X | 120/1 | < 60 | C,E,G | Electric actuator for chemical service
Polymer System FSL RDT
Polymer fill to tank TK-C401 isolation valve | XV-C4014 | 1-0102-PPID-C401 | Ball | V330 | 50 | MP | Mixed Polymer |  | 1.25 | O/C | 4X | 120/1 | < 60 | J | Electric actuator for chemical service - by skid supplier
Polymer fill to tank TK-C402 isolation valve | XV-C4024 | 1-0102-PPID-C401 | Ball | V330 | 50 | MP | Mixed Polymer |  | 1.25 | O/C | 4X | 120/1 | < 60 | J | Electric actuator for chemical service - by skid supplier
Polymer fill to tank TK-C403 isolation valve | XV-C4034 | 1-0102-PPID-C401 | Ball | V330 | 50 | MP | Mixed Polymer |  | 1.25 | O/C | 4X | 120/1 | < 60 | J | Electric actuator for chemical service - by skid supplier
Polymer fill to tank TK-C402 isolation valve | XV-C4025 | 1-0102-PPID-C401 | Ball | V330 | 50 | MP | Mixed Polymer |  |  | O/C | 4X | 120/1 | < 60 | J | Electric actuator for chemical service - by skid supplier
Polymer fill to tank TK-C403 isolation valve | XV-C4035 | 1-0102-PPID-C401 | Ball | V330 | 50 | MP | Mixed Polymer |  |  | O/C | 4X | 120/1 | < 60 | J | Electric actuator for chemical service - by skid supplier
Aging tanks interconnection isolation valve | XV-C4037 | 1-0102-PPID-C401 | Ball | V330 | 50 | MP | Mixed Polymer |  |  | O/C | 4X | 120/1 | < 60 | J | Electric actuator for chemical service - by skid supplier
Aging tank TK-C402 outlet isolation valve | XV-C4026 | 1-0102-PPID-C401 | Ball | V330 | 50 | MP | Mixed Polymer |  |  | O/C | 4X | 120/1 | < 60 | J | Electric actuator for chemical service - by skid supplier
Aging tank TK-C403 outlet isolation valve | XV-C4036 | 1-0102-PPID-C401 | Ball | V330 | 50 | MP | Mixed Polymer |  |  | O/C | 4X | 120/1 | < 60 | J | Electric actuator for chemical service - by skid supplier
Flushing service water dilution isolation valve | FV-C4162 | 1-0102-PPID-C402 | Ball | V307 | 75 | FSW | Flushing Water |  |  | O/C | 4X | 120/1 | < 60 | C,E,G | Electric actuator for chemical service
Flushing service water dilution isolation valve | FV-C4172 | 1-0102-PPID-C403 | Ball | V307 | 75 | FSW | Flushing Water |  |  | O/C | 4X | 120/1 | < 60 | C,E,G | Electric actuator for chemical service
Flushing service water dilution isolation valve | FV-C4182 | 1-0102-PPID-C404 | Ball | V307 | 75 | FSW | Flushing Water |  |  | O/C | 4X | 120/1 | < 60 | C,E,G | Electric actuator for chemical service
Polymer skid pump P-C414 isolation valve | XV-C4145 | 1-0102-PPID-C403 | Ball | V330 | 50 | MP | Mixed Polymer |  |  | O/C | 4X | 120/1 | < 60 | C,F | Electric actuator for chemical service - by skid supplier
Polymer skid pump P-C414 isolation valve | XV-C4146 | 1-0102-PPID-C403 | Ball | V330 | 50 | MP | Mixed Polymer |  |  | O/C | 4X | 120/1 | < 60 | C,F | Electric actuator for chemical service - by skid supplier
Polymer System WAS RDT
Polymer fill to tank TK-C421 isolation valve | XV-C4212 | 1-0102-PPID-C405 | Ball | V330 | 25 | MP | Mixed Polymer |  |  | O/C | 4X | 120/1 | < 60 | J | Electric actuator for chemical service - by skid supplier
Polymer fill to tank TK-C422 isolation valve | XV-C4222 | 1-0102-PPID-C405 | Ball | V330 | 25 | MP | Mixed Polymer |  |  | O/C | 4X | 120/1 | < 60 | J | Electric actuator for chemical service - by skid supplier
Polymer fill to tank TK-C422 isolation valve | XV-C4223 | 1-0102-PPID-C405 | Ball | V330 | 50 | MP | Mixed Polymer |  |  | O/C | 4X | 120/1 | < 60 | J | Electric actuator for chemical service - by skid supplier
Flushing service water dilution isolation valve | FV-C4362 | 1-0102-PPID-C406 | Ball | V307 | 50 | FSW | Flushing Water |  |  | O/C | 4X | 120/1 | < 60 | C,E,G | Electric actuator for chemical service
Flushing service water dilution isolation valve | FV-C4372 | 1-0102-PPID-C407 | Ball | V307 | 50 | FSW | Flushing Water |  |  | O/C | 4X | 120/1 | < 60 | C,E,G | Electric actuator for chemical service
Polymer skid pump P-C432 isolation valve | XV-C4325 | 1-0102-PPID-C406 | Ball | V330 | 50 | MP | Mixed Polymer |  |  | O/C | 4X | 120/1 | < 60 | C,F | Electric actuator for chemical service - by skid supplier
Polymer skid pump P-C432 isolation valve | XV-C4326 | 1-0102-PPID-C406 | Ball | V330 | 50 | MP | Mixed Polymer |  |  | O/C | 4X | 120/1 | < 60 | C,F | Electric actuator for chemical service - by skid supplier
Polymer System HRC
Polymer fill to tank TK-C441 isolation valve | XV-C4414 | 1-0102-PPID-C408 | Ball | V330 | 50 | MP | Mixed Polymer |  |  | O/C | 4X | 120/1 | < 60 | J | Electric actuator for chemical service - by skid supplier
Polymer fill to tank TK-C442 isolation valve | XV-C4424 | 1-0102-PPID-C408 | Ball | V330 | 50 | MP | Mixed Polymer |  |  | O/C | 4X | 120/1 | < 60 | J | Electric actuator for chemical service - by skid supplier
Polymerr fill to tank TK-C443 isolation valve | XV-C4434 | 1-0102-PPID-C408 | Ball | V330 | 50 | MP | Mixed Polymer |  |  | O/C | 4X | 120/1 | < 60 | J | Electric actuator for chemical service - by skid supplier
Polymer fill to tank TK-C442 isolation valve | XV-C4425 | 1-0102-PPID-C408 | Ball | V330 | 50 | MP | Mixed Polymer |  |  | O/C | 4X | 120/1 | < 60 | J | Electric actuator for chemical service - by skid supplier
Polymer fill to tank TK-C443 isolation valve | XV-C4435 | 1-0102-PPID-C408 | Ball | V330 | 50 | MP | Mixed Polymer |  |  | O/C | 4X | 120/1 | < 60 | J | Electric actuator for chemical service - by skid supplier
Aging tanks interconnection isolation valve | XV-C4437 | 1-0102-PPID-C408 | Ball | V330 | 50 | MP | Mixed Polymer |  |  | O/C | 4X | 120/1 | < 60 | J | Electric actuator for chemical service - by skid supplier
Aging tank TK-C442 outlet isolation valve | XV-C4426 | 1-0102-PPID-C408 | Ball | V330 | 50 | MP | Mixed Polymer |  |  | O/C | 4X | 120/1 | < 60 | J | Electric actuator for chemical service - by skid supplier
Aging tank TK-C442 outlet isolation valve | XV-C4436 | 1-0102-PPID-C408 | Ball | V330 | 50 | MP | Mixed Polymer |  |  | O/C | 4X | 120/1 | < 60 | J | Electric actuator for chemical service - by skid supplier
Tank TK-C441 outlet isolation valve | XV-C4415 | 1-0102-PPID-C408 | Ball | V330 | 50 | MP | Mixed Polymer |  |  | O/C | 4X | 120/1 | < 60 | J | Electric actuator for chemical service - by skid supplier
Tanks feed pipe to pumps isolation valve | XV-C4416 | 1-0102-PPID-C408 | Ball | V330 | 50 | MP | Mixed Polymer |  |  | O/C | 4X | 120/1 | < 60 | J | Electric actuator for chemical service - by skid supplier
Non Potable Water Supply pipe | XV-C4417 | 1-0102-PPID-C408 | Ball | V307 | 25 | NPT | Non-Potable Tempered Water |  |  | O/C | 4X | 120/1 | < 60 | J | Electric actuator for chemical service - by skid supplier
Flushing service water dilution isolation valve | FV-C4562 | 1-0102-PPID-C409 | Ball | V307 | 75 | FSW | Flushing Water |  |  | O/C | 4X | 120/1 | < 60 | C,E,G | Electric actuator for chemical service
Polymer feed to HRC Train 1 isolation valve | XV-C4563 | 1-0102-PPID-C409 | Ball | V330 | 75 | MP | Mixed Polymer |  |  | O/C | 4X | 120/1 | < 60 | C,F | Electric actuator for chemical service
Polymer feed to mixed liquor channel | XV-C4564 | 1-0102-PPID-C409 | Ball | V330 | 75 | MP | Mixed Polymer |  |  | O/C | 4X | 120/1 | < 60 | C,F | Electric actuator for chemical service
Flushing service water dilution isolation valve | FV-C4572 | 1-0102-PPID-C410 | Ball | V307 | 75 | FSW | Flushing Water |  |  | O/C | 4X | 120/1 | < 60 | C,E,G | Electric actuator for chemical service
Polymer feed to HRC Train 2 isolation valve | XV-C4573 | 1-0102-PPID-C410 | Ball | V330 | 75 | MP | Mixed Polymer |  |  | O/C | 4X | 120/1 | < 60 | C,F | Electric actuator for chemical service
Polymer feed to mixed liquor channel | XV-C4574 | 1-0102-PPID-C410 | Ball | V330 | 75 | MP | Mixed Polymer |  |  | O/C | 4X | 120/1 | < 60 | C,F | Electric actuator for chemical service
Polymer skid pump P-C452 isolation valve | XV-C4525 | 1-0102-PPID-C406 | Ball | V330 | 50 | MP | Mixed Polymer |  |  | O/C | 4X | 120/1 | < 60 | C,F | Electric actuator for chemical service - by skid supplier
Polymer skid pump P-C452 isolation valve | XV-C4526 | 1-0102-PPID-C406 | Ball | V330 | 50 | MP | Mixed Polymer |  |  | O/C | 4X | 120/1 | < 60 | C,F | Electric actuator for chemical service - by skid supplier
Polymer System Secondary Clarifiers
Polymer fill to tank TK-C461 isolation valve | XV-C4612 | 1-0102-PPID-C411 | Ball | V330 | 25 | MP | Mixed Polymer |  |  | O/C | 4X | 120/1 | < 60 | J | Electric actuator for chemical service - by skid supplier
Polymer fill to tank TK-C462 isolation valve | XV-C4622 | 1-0102-PPID-C411 | Ball | V330 | 25 | MP | Mixed Polymer |  |  | O/C | 4X | 120/1 | < 60 | J | Electric actuator for chemical service - by skid supplier
Polymer fill to tank TK-C462 isolation valve | XV-C4623 | 1-0102-PPID-C411 | Ball | V330 | 50 | MP | Mixed Polymer |  |  | O/C | 4X | 120/1 | < 60 | J | Electric actuator for chemical service - by skid supplier
Flushing service water dilution isolation valve | FV-C4762 | 1-0102-PPID-C412 | Ball | V307 | 75 | FSW | Flushing Water |  |  | O/C | 4X | 120/1 | < 60 | C,E,G | Electric actuator for chemical service
Non Potable Water
Non Potable Water to Polymer Makedown Systems | FV-C5101 | 1-0102-PPID-C504 | Ball | V307 | 100 | NPT | Non-Potable Tempered Water |  |  | O/C | 4X | 120/1 | < 60 | C,E,G | Electric actuator for chemical service
AREA Y - YARD / ELECTRICAL SUBSTATION
AREA B - SERVICE BUILDING
AREA M - ADMINISTRATION BUILDING
BUILDING MECHANICAL
AREA G - HEADWORKS
Propylene glycol to AHU-G610 | TV-G6106 | 1-0102-PPID-G617 | Three-way | V240 | 65 | GS | Glycol Supply | 35 | 8.82 | M | 1 | 24 | <60 | C,G
Propylene glycol to AHU-G620 | TV-G6206 | 1-0102-PPID-G608 | Three-way | V240 | 100 | GS | Glycol Supply | 35 | 15.91 | M | 1 | 24 | <60 | C,G
Propylene glycol to AHU-G630 | TV-G6306 | 1-0102-PPID-G618 | Three-way | V240 | 65 | GS | Glycol Supply | 35 | 7.34 | M | 1 | 24 | <60 | C,G
Propylene glycol from HE-G663 | TV-G6631 | 1-0102-PPID-G625 | Three-way | V240 | 125 | HWR | Hot Water Return | 35 | 29.4 | M | 1 | 24 | <60 | C,G
Flushing water for Glycol Heat Recovery | TV-G6731 | 1-0102-PPID-G623 | Two-way | V307 | 100 | FSW | Flushing Water |  |  | O/C |  |  | <60
Flushing water for Heat Pump Condenser Water | TV-G6761 | 1-0102-PPID-G623 | Three-way | V240 | 75 | CDR | Condenser Water |  |  | M |  |  | <60
AREA P - PRIMARY CLARIFIERS
AREA R - BIOREACTORS / BLOWER BUILDING
Propylene glycol to AHU-R610 | TV-R6202 | 1-0102-PPID-R604 | Three-way | V240 | 65 | GS | Glycol Supply | 30 | 4.73 | O/C | 1 | 24 | <60 | C,G | Electric actuator by valve supplier
EF-R601 Inlet | XV-R6011 | 1-0102-PPID-R602 | Isolation Damper | V965 | 1000 | FOA | Foul Air |  |  | O/C | 8 | 600/3 | ≤ 30 | C,D | Explosion Proof, Class 1 Div 2
EF-R602 Inlet | XV-R6021 | 1-0102-PPID-R602 | Isolation Damper | V965 | 1000 | FOA | Foul Air |  |  | O/C | 8 | 600/3 | ≤ 30 | C,D | Explosion Proof, Class 1 Div 2
AREA S - SECONDARY CLARIFIERS
Flushing for glycol heat recovery system | XV-S6634 | 1-0102-PPID-S627 | Two-way | V307 | 100 | FSW | Flushing Water | 30 |  | O/C | 1 | 24 | <60 | C,G | Electric actuator by valve supplier
Backwash drain for flushing water automatic strainer | XV-S6732 | 1-0102-PPID-S627 | Two-way | V308 | 25 | FSW | Flushing Water | 30 |  | O/C | 1 | 24 | <60 | J | Electric actuator by valve supplier
Backwash drain for flushing water automatic strainer | XV-S6742 | 1-0102-PPID-S627 | Two-way | V308 | 25 | FSW | Flushing Water | 30 |  | O/C | 1 | 24 | <60 | J | Electric actuator by valve supplier
AREA U - UV DISINFECTION BUILDING
AREA K - HIGH RATE CLARIFIERS
Propylene glycol to AHU-K610 | TV-K6104 | 1-0102-PPID-K601 | Three-way | V240 | 75 | GS | Glycol Supply | 35 | 8.44 | M | 1 | 24 | <60 | C,G | Electric actuator by valve supplier
Propylene glycol to AHU-K620 | TV-K6204 | 1-0102-PPID-K602 | Three-way | V240 | 50 | GS | Glycol Supply | 35 | 2.95 | M | 1 | 24 | <60 | C,G | Electric actuator by valve supplier
Propylene glycol to AHU-K630 | TV-K6304 | 1-0102-PPID-K603 | Three-way | V240 | 50 | GS | Glycol Supply | 35 | 3.31 | M | 1 | 24 | <60 | C,G | Electric actuator by valve supplier
Propylene glycol to AHU-K640 | TV-K6404 | 1-0102-PPID-K604 | Three-way | V240 | 32 | GS | Glycol Supply | 35 | 0.33 | M | 1 | 24 | <60 | C,G | Electric actuator by valve supplier
Propylene glycol to HE-K663 | TV-K6631 | 1-0102-PPID-K606 | Three-way | V240 | 75 | HWR | Hot Water Return | 35 | 13.8 | M | 1 | 24 | <60 | C,G | Electric actuator by valve supplier
AREA D - FERMENTERS / THICKENERS
AREA T - BIOFILTER / ODOUR CONTROL
AREA C - CHEMICAL BUILDING / ELECTRICAL BUILDING
AREA Y - YARD / ELECTRICAL SUBSTATION
AREA B - SERVICE BUILDING
AREA M - ADMINISTRATION BUILDING
General Notes:
1. This schedule is provided for the Contractor's convenience and shall not be taken as complete.
2. Valves to be supplied and installed under this contract unless otherwise indicated.
3. n/a = not applicable; valve supplied by others, installed under this contract.
4. Refer to the scope of pre-purchased equipment for valves that are supplied by others to be installed under this contract.
Notes:
1. Service:
O/C = Open-Close
T = Throttling
M = Modulating
2. Control Features:
A = Actuator shall open valve upon loss of signal.
B = Actuator shall close valve upon loss of signal.
C = Actuator shall maintain valve in last position upon loss of signal.
D = Local LOCAL-REMOTE hand switch with local OPEN-CLOSE momentary pushbuttons that must be continuously depressed to initiate/maintain valve travel; travel stops when pushbutton is released, or when end of travel limit is reached.
E = Remote OPEN-CLOSE maintained control signal; travel stops when end of travel limit is reached.
F = Local LOCAL-REMOTE hand switch with local OPEN-CLOSE hand switch and remote OPEN-CLOSE maintained control signal; travel stops when LOCAL mode selected, or when end of travel limit is reached.
G = Valve position controlled by a modulating analog signal with feedback signal in proportion to valve position, either through a PROFIBUS DP interface or 4-20 mA signals.
H = PROFIBUS DP option card required
I = Modbus RTU option card required
J = Control features as per packaged system vendor requirements
Bottom of print range

## Solenoid
SEWPCC UPGRADING/EXPANSION PROJECT
Solenoid Valve Schedule
Location / Description | Tag Number | P&ID Number | Valve Type | Valve Type Number | Size (mm) | Commodity Code | Commodity | Maximum DP (kPa) | Maximum Flow (L/s) | NEMA Rating | Control Features [Note 1] | Remarks
PROCESS MECHANICAL
AREA G - HEADWORKS
Raw Sewage Pumping
Seal Water to Raw Sewage Pump P-G102 | YV-G1023 | 1-0102-PPID-G103 | Solenoid | V940 | 12 | NPW | Non-Potable Water |  |  | 4 | NC,B
Grit Removal
Seal Water to Grit Slurry Pump P-G323 | YV-G3235 | 1-0102-PPID-G302 | Solenoid | V940 | 12 | NPW | Non-Potable Water |  | 0.1 | 4 | NC,B
Seal Water to Grit Slurry Pump P-G324 | YV-G3245 | 1-0102-PPID-G302 | Solenoid | V940 | 12 | NPW | Non-Potable Water |  | 0.1 | 4 | NC,B
Seal Water to Grit Slurry Pump P-G325 | YV-G3255 | 1-0102-PPID-G302 | Solenoid | V940 | 12 | NPW | Non-Potable Water |  | 0.1 | 4 | NC,B
Wash Water
Wash Water to Washer/Compactor WCP-G231 | XV-G2314 | 1-0102-PPID-G203 | Solenoid | V940 | 25 | FSW | Flushing Water |  |  | 4 | J | Supplied by washer/compactor vendor.
Wash Water to Washer/Compactor WCP-G232 | XV-G2324 | 1-0102-PPID-G203 | Solenoid | V940 | 25 | FSW | Flushing Water |  |  | 4 | J | Supplied by washer/compactor vendor.
AREA R - BIOREACTORS / BLOWER BUILDING
Instrument Panel Instrument Air | XV-R1041-1 | 1-0102-PPID-R109 | Solenoid | V940 | 25 | IAS | Instrument Air Supply |  |  | 4X | NC,B | Coordinate with instrument vendor and size accordingly
Instrument Panel Instrument Air | XV-R1041-2 | 1-0102-PPID-R109 | Solenoid | V940 | 25 | IAS | Instrument Air Supply |  |  | 4X | NC,B | Coordinate with instrument vendor and size accordingly
Instrument Panel Instrument Air | XV-R1022 | 1-0102-PPID-R109 | Solenoid | V940 | 25 | IAS | Instrument Air Supply |  |  | 4X | NC,B | Coordinate with instrument vendor and size accordingly
Instrument Panel Instrument Air | XV-R1032 | 1-0102-PPID-R109 | Solenoid | V940 | 25 | IAS | Instrument Air Supply |  |  | 4X | NC,B | Coordinate with instrument vendor and size accordingly
Instrument Panel Instrument Air | XV-R1051 | 1-0102-PPID-R109 | Solenoid | V940 | 25 | IAS | Instrument Air Supply |  |  | 4X | NC,B | Coordinate with instrument vendor and size accordingly
Instrument Panel Instrument Air | XV-R1052 | 1-0102-PPID-R109 | Solenoid | V940 | 25 | IAS | Instrument Air Supply |  |  | 4X | NC,B | Coordinate with instrument vendor and size accordingly
Instrument Panel Instrument Air | XV-R1141-1 | 1-0102-PPID-R109 | Solenoid | V940 | 25 | IAS | Instrument Air Supply |  |  | 4X | NC,B | Coordinate with instrument vendor and size accordingly
Instrument Panel Instrument Air | XV-R1141-2 | 1-0102-PPID-R109 | Solenoid | V940 | 25 | IAS | Instrument Air Supply |  |  | 4X | NC,B | Coordinate with instrument vendor and size accordingly
Instrument Panel Instrument Air | XV-R1122 | 1-0102-PPID-R109 | Solenoid | V940 | 25 | IAS | Instrument Air Supply |  |  | 4X | NC,B | Coordinate with instrument vendor and size accordingly
Instrument Panel Instrument Air | XV-R1132 | 1-0102-PPID-R109 | Solenoid | V940 | 25 | IAS | Instrument Air Supply |  |  | 4X | NC,B | Coordinate with instrument vendor and size accordingly
Instrument Panel Instrument Air | XV-R1151 | 1-0102-PPID-R109 | Solenoid | V940 | 25 | IAS | Instrument Air Supply |  |  | 4X | NC,B | Coordinate with instrument vendor and size accordingly
Instrument Panel Instrument Air | XV-R1152 | 1-0102-PPID-R109 | Solenoid | V940 | 25 | IAS | Instrument Air Supply |  |  | 4X | NC,B | Coordinate with instrument vendor and size accordingly
Instrument Panel Instrument Air | XV-R1241-1 | 1-0102-PPID-R109 | Solenoid | V940 | 25 | IAS | Instrument Air Supply |  |  | 4X | NC,B | Coordinate with instrument vendor and size accordingly
Instrument Panel Instrument Air | XV-R1241-2 | 1-0102-PPID-R109 | Solenoid | V940 | 25 | IAS | Instrument Air Supply |  |  | 4X | NC,B | Coordinate with instrument vendor and size accordingly
Instrument Panel Instrument Air | XV-R1222 | 1-0102-PPID-R109 | Solenoid | V940 | 25 | IAS | Instrument Air Supply |  |  | 4X | NC,B | Coordinate with instrument vendor and size accordingly
Instrument Panel Instrument Air | XV-R1232 | 1-0102-PPID-R109 | Solenoid | V940 | 25 | IAS | Instrument Air Supply |  |  | 4X | NC,B | Coordinate with instrument vendor and size accordingly
Instrument Panel Instrument Air | XV-R1251 | 1-0102-PPID-R109 | Solenoid | V940 | 25 | IAS | Instrument Air Supply |  |  | 4X | NC,B | Coordinate with instrument vendor and size accordingly
Instrument Panel Instrument Air | XV-R1252 | 1-0102-PPID-R109 | Solenoid | V940 | 25 | IAS | Instrument Air Supply |  |  | 4X | NC,B | Coordinate with instrument vendor and size accordingly
AREA S - SECONDARY CLARIFIERS
Seal Water to RAS Pump P-S216 | YV-S2163 | 1-0102-PPID-S204 | Solenoid | V940 | 12 | NPW | Non-Potable Water |  |  | 4X | NC,B
Seal Water to RAS Pump P-S217 | YV-S2173 | 1-0102-PPID-S205 | Solenoid | V940 | 12 | NPW | Non-Potable Water |  |  | 4X | NC,B
Seal Water to RAS Pump P-S218 | YV-S2183 | 1-0102-PPID-S205 | Solenoid | V940 | 12 | NPW | Non-Potable Water |  |  | 4X | NC,B
Seal Water to Scum Pump P-S316 | YV-S3161 | 1-0102-PPID-S303 | Solenoid | V940 | 12 | NPW | Non-Potable Water |  |  | 4X | NC,B
Seal Water to Scum Pump P-S317 | YV-S3171 | 1-0102-PPID-S303 | Solenoid | V940 | 12 | NPW | Non-Potable Water |  |  | 4X | NC,B
Seal Water to Flushing Water Pump P-S550 | YV-S5501 | 1-0102-PPID-S506 | Solenoid | V940 | 12 | NPW | Non-Potable Water |  |  | 4X | NC,B
Instrument Air Supply | XV-S5408 | 1-0102-PPID-S107 | Solenoid | V940 | - | IAS | Instrument Air Supply |  |  | 4X | J | Supplied by Package Sampler Vendor
AREA U - UV DISINFECTION BUILDING
UV system lamp service system | XV-U2111 | 1-0102-PPID-U201 | Solenoid | - | [5 empty] | 4X | J | Supplied by UV Vendor
UV system lamp service system | XV-U2112 | 1-0102-PPID-U201 | Solenoid | - | [5 empty] | 4X | J | Supplied by UV Vendor
UV system lamp service system | XV-U2121 | 1-0102-PPID-U201 | Solenoid | - | [5 empty] | 4X | J | Supplied by UV Vendor
UV system lamp service system | XV-U2122 | 1-0102-PPID-U201 | Solenoid | - | [5 empty] | 4X | J | Supplied by UV Vendor
UV system lamp service system | XV-U2131 | 1-0102-PPID-U201 | Solenoid | - | [5 empty] | 4X | J | Supplied by UV Vendor
UV system lamp service system | XV-U2132 | 1-0102-PPID-U201 | Solenoid | - | [5 empty] | 4X | J | Supplied by UV Vendor
UV system lamp service system | XV-U2141 | 1-0102-PPID-U201 | Solenoid | - | [5 empty] | 4X | J | Supplied by UV Vendor
UV system lamp service system | XV-U2142 | 1-0102-PPID-U201 | Solenoid | - | [5 empty] | 4X | J | Supplied by UV Vendor
UV system lamp service system | XV-U2151 | 1-0102-PPID-U201 | Solenoid | - | [5 empty] | 4X | J | Supplied by UV Vendor
UV system lamp service system | XV-U2152 | 1-0102-PPID-U201 | Solenoid | - | [5 empty] | 4X | J | Supplied by UV Vendor
UV system lamp service system | XV-U2211 | 1-0102-PPID-U202 | Solenoid | - | [5 empty] | 4X | J | Supplied by UV Vendor
UV system lamp service system | XV-U2212 | 1-0102-PPID-U202 | Solenoid | - | [5 empty] | 4X | J | Supplied by UV Vendor
UV system lamp service system | XV-U2221 | 1-0102-PPID-U202 | Solenoid | - | [5 empty] | 4X | J | Supplied by UV Vendor
UV system lamp service system | XV-U2222 | 1-0102-PPID-U202 | Solenoid | - | [5 empty] | 4X | J | Supplied by UV Vendor
UV system lamp service system | XV-U2231 | 1-0102-PPID-U202 | Solenoid | - | [5 empty] | 4X | J | Supplied by UV Vendor
UV system lamp service system | XV-U2232 | 1-0102-PPID-U202 | Solenoid | - | [5 empty] | 4X | J | Supplied by UV Vendor
UV system lamp service system | XV-U2241 | 1-0102-PPID-U202 | Solenoid | - | [5 empty] | 4X | J | Supplied by UV Vendor
UV system lamp service system | XV-U2242 | 1-0102-PPID-U202 | Solenoid | - | [5 empty] | 4X | J | Supplied by UV Vendor
UV system lamp service system | XV-U2251 | 1-0102-PPID-U202 | Solenoid | - | [5 empty] | 4X | J | Supplied by UV Vendor
UV system lamp service system | XV-U2252 | 1-0102-PPID-U202 | Solenoid | - | [5 empty] | 4X | J | Supplied by UV Vendor
AREA K - HIGH RATE CLARIFIERS
Non-Potable Water for Flushing HRC Train 1 Sample Line | XV-K1156 | 1-0102-PPID-K106 | Solenoid | - | 20 | NPW | Non-Potable Water |  |  | 4X | NC,B
Non-Potable Water for Flushing HRC Train 2 Sample Line | XV-K1256 | 1-0102-PPID-K106 | Solenoid | - | 20 | NPW | Non-Potable Water |  |  | 4X | NC,B
Air Scour to HRC Train 1 North Corner Grid | XV-K1141 | 1-0102-PPID-K108 | Solenoid | - | 50 | ALP | Air, Low Pressure |  |  | - | J | Supplied by HRC vendor
Air Scour to HRC Train 1 South Corner Grid | XV-K1142 | 1-0102-PPID-K108 | Solenoid | - | 50 | ALP | Air, Low Pressure |  |  | - | J | Supplied by HRC vendor
Air Scour to HRC Train 1 Rotating Grid | XV-K1143 | 1-0102-PPID-K108 | Solenoid | - | 50 | ALP | Air, Low Pressure |  |  | - | J | Supplied by HRC vendor
Air Scour to HRC Train 2 North Corner Grid | XV-K1241 | 1-0102-PPID-K108 | Solenoid | - | 50 | ALP | Air, Low Pressure |  |  | - | J | Supplied by HRC vendor
Air Scour to HRC Train 2 South Corner Grid | XV-K1242 | 1-0102-PPID-K108 | Solenoid | - | 50 | ALP | Air, Low Pressure |  |  | - | J | Supplied by HRC vendor
Air Scour to HRC Train 2 Rotating Grid | XV-K1243 | 1-0102-PPID-K108 | Solenoid | - | 50 | ALP | Air, Low Pressure |  |  | - | J | Supplied by HRC vendor
Ballast Addition Skid Non-Potable Water Control | XV-K3105 | 1-0102-PPID-K301 | Solenoid | - | 50 | NPW | Non-Potable Water |  |  | - | J | Supplied by HRC vendor as part of Ballast Addition Skid
Ballast Addition Skid Non-Potable Water Control | XV-K3106 | 1-0102-PPID-K301 | Solenoid | - | 6 | NPW | Non-Potable Water |  |  | - | J | Supplied by HRC vendor as part of Ballast Addition Skid
AREA D - FERMENTERS / THICKENERS
Seal Water to Fermenter Recirculation Pump P-D321 | YV-D3213 | 1-0102-PPID-D303 | Solenoid | V940 | 12 | NPW | Non-Potable Water |  |  | 4X | NC,B
Seal Water to Fermenter Recirculation Pump P-D322 | YV-D3223 | 1-0102-PPID-D303 | Solenoid | V940 | 12 | NPW | Non-Potable Water |  |  | 4X | NC,B
Seal Water to Fermenter Recirculation Pump P-D323 | YV-D3233 | 1-0102-PPID-D303 | Solenoid | V940 | 12 | NPW | Non-Potable Water |  |  | 4X | NC,B
AREA T - BIOFILTER / ODOUR CONTROL
Natural Gas Supply to Glycol Heater | XV-T1063 | 1-0102-PPID-T102 | Solenoid | - | 32 | NG | Natural Gas |  |  | - | J | Supplied by Biofilter vendor, explosion proof
Natural Gas Supply to Glycol Heater | XV-T1064 | 1-0102-PPID-T102 | Solenoid | - | 32 | NG | Natural Gas |  |  | - | J | Supplied by Biofilter vendor, explosion proof
Humidifier Tower HUM-T110 Washer Sprays Inlet | XV-T1101 | 1-0102-PPID-T103 | Solenoid | - | 12 | FSW | Flushing Water |  |  | - | J | Supplied by Biofilter vendor, explosion proof
Humidifier Tower HUM-T120 Washer Sprays Inlet | XV-T1201 | 1-0102-PPID-T105 | Solenoid | - | 12 | FSW | Flushing Water |  |  | - | J | Supplied by Biofilter vendor, explosion proof
AREA C - CHEMICAL BUILDING / ELECTRICAL BUILDING
Non-potable Tempered Water to FPS/HRC Polymer Make Down System | XV-C4043 | 1-0102-PPID-C401 | Solenoid | - | - | NPT | Non-Potable Tempered Water |  |  | - | J | Supplied by Polymer Make Down Vendor
Non-potable Tempered Water to FPS/HRC Polymer Make Down System | XV-C4044 | 1-0102-PPID-C401 | Solenoid | - | - | NPT | Non-Potable Tempered Water |  |  | - | J | Supplied by Polymer Make Down Vendor
Non-potable Tempered Water to WAS Polymer Make Down System | XV-C4243 | 1-0102-PPID-C405 | Solenoid | - | - | NPT | Non-Potable Tempered Water |  |  | - | J | Supplied by Polymer Make Down Vendor
Non-potable Tempered Water to WAS Polymer Make Down System | XV-C4244 | 1-0102-PPID-C405 | Solenoid | - | - | NPT | Non-Potable Tempered Water |  |  | - | J | Supplied by Polymer Make Down Vendor
Non-potable Tempered Water to HRC Polymer Make Down System | XV-C4441 | 1-0102-PPID-C408 | Solenoid | - | - | NPT | Non-Potable Tempered Water |  |  | - | J | Supplied by Polymer Make Down Vendor
Non-potable Tempered Water to HRC Polymer Make Down System | XV-C4442 | 1-0102-PPID-C408 | Solenoid | - | - | NPT | Non-Potable Tempered Water |  |  | - | J | Supplied by Polymer Make Down Vendor
Non-potable Tempered Water to Secondary Clarifier Polymer Make Down System | XV-C4643 | 1-0102-PPID-C411 | Solenoid | - | - | NPT | Non-Potable Tempered Water |  |  | - | J | Supplied by Polymer Make Down Vendor
Non-potable Tempered Water to Secondary Clarifier Make Down System | XV-C4644 | 1-0102-PPID-C411 | Solenoid | - | - | NPT | Non-Potable Tempered Water |  |  | - | J | Supplied by Polymer Make Down Vendor
Diesel Fuel Supply from P-C561 Pump | XV-C5611 | 1-0102-PPID-C510 | Solenoid | - | - | DFS | Diesel Fuel Supply |  |  | - | J | Supplied by Diesel Fuel Storage System Vendor
Diesel Fuel Supply from P-C562 Pump | XV-C5621 | 1-0102-PPID-C510 | Solenoid | - | - | DFS | Diesel Fuel Supply |  |  | - | J | Supplied by Diesel Fuel Storage System Vendor
Diesel Fuel Supply to Tank TK-C570 | XV-C5705 | 1-0102-PPID-C511 | Solenoid | - | - | DFS | Diesel Fuel Supply |  |  | - | J | Supplied by Diesel Fuel Storage System Vendor
Diesel Fuel Supply to Tank TK-C580 | XV-C5805 | 1-0102-PPID-C512 | Solenoid | - | - | DFS | Diesel Fuel Supply |  |  | - | J | Supplied by Diesel Fuel Storage System Vendor
General Notes:
1. This schedule is provided for the Contractor's convenience and shall not be taken as complete.
2. Valves to be supplied and installed under this contract unless otherwise indicated.
3. n/a = not applicable; valve supplied by others, installed under this contract.
4. Refer to the scope of pre-purchased equipment for valves that are supplied by others to be installed under this contract.
Notes:
1. Control Features:
NO = Open when de-energized
NC = Closed when de-energized
A = Slow closing
B = Manual override button
J = Control features as per packaged system vendor requirements
Bottom of print range

## Self-contained
SEWPCC UPGRADING/EXPANSION PROJECT
Self-Contained Valve Schedule
Description / Location | Tag Number | P&ID Number | Valve Type | Valve Type Number | Size (mm) | Commodity Code | Commodity | Inlet Pressure (kPag) [Note 1] | Outlet Pressure (kPag) | Maximum Flow (L/s) | Remarks
PROCESS MECHANICAL
AREA G - HEADWORKS
Raw Sewage Pumping
Seal Water to Raw Sewage Pump P-G102 | PCV-G1029 | 1-0102-PPID-G103 | Pressure reducing | V711 | 12 | NPW | Non-Potable Water | 685-750 | 250 | 0.1
Grit Removal
Flushing Water to Grit Tank 1 | PCV-G3219 | 1-0102-PPID-G301 | Pressure reducing | V711 | 25 | FSW | Flushing Water | 685-750 | 60 | 1.3
Flushing Water to Grit Tank 2 | PCV-G3229 | 1-0102-PPID-G301 | Pressure reducing | V711 | 25 | FSW | Flushing Water | 685-750 | 60 | 1.3
Seal Water to Grit Slurry Pump P-G323 | PCV-G3239 | 1-0102-PPID-G302 | Pressure reducing | V711 | 12 | NPW | Non-Potable Water | 685-750 | 350 | 0.1
Seal Water to Grit Slurry Pump P-G324 | PCV-G3249 | 1-0102-PPID-G302 | Pressure reducing | V711 | 12 | NPW | Non-Potable Water | 685-750 | 350 | 0.1
Seal Water to Grit Slurry Pump P-G325 | PCV-G3259 | 1-0102-PPID-G302 | Pressure reducing | V711 | 12 | NPW | Non-Potable Water | 685-750 | 350 | 0.1
Wash Water
Wash Water to Screen SCR-G211 | PCV-G2119 | 1-0102-PPID-G201 | Pressure reducing | V711 | 38 | FSW | Flushing Water | 685-750 | 410 | 2.5
Wash Water to Screen SCR-G212 | PCV-G2129 | 1-0102-PPID-G201 | Pressure reducing | V711 | 38 | FSW | Flushing Water | 685-750 | 410 | 2.5
Wash Water to Screen SCR-G213 | PCV-G2139 | 1-0102-PPID-G202 | Pressure reducing | V711 | 38 | FSW | Flushing Water | 685-750 | 410 | 2.5
Wash Water to Screen SCR-G214 | PCV-G2149 | 1-0102-PPID-G202 | Pressure reducing | V711 | 38 | FSW | Flushing Water | 685-750 | 410 | 2.5
Wash Water to Washer/Compactor WCP-G231 | PCV-G2319 | 1-0102-PPID-G203 | Pressure reducing | V711 | 25 | FSW | Flushing Water | 685-750 | 410 | 3
Wash Water to Washer/Compactor WCP-G232 | PCV-G2329 | 1-0102-PPID-G203 | Pressure reducing | V711 | 25 | FSW | Flushing Water | 685-750 | 410 | 3
Wash Water to Grit Classifier GRP-G341 | PCV-G3419 | 1-0102-PPID-G305 | Pressure reducing | V711 | 25 | FSW | Flushing Water | 685-750 | 150 | 0.5
Wash Water to Grit Classifier GRP-G342 | PCV-G3429 | 1-0102-PPID-G305 | Pressure reducing | V711 | 25 | FSW | Flushing Water | 685-750 | 150 | 0.5
AREA R - BIOREACTORS / BLOWER BUILDING
FSF Pipe | N/A | 1-0102-PPID-R101 | Air release | V752 | 50 | FSF | Fermented Sludge Filtrate | 80-120
Ferric Chloride Application Point for bioreactor 1 | PCV-R1059 | 1-0102-PPID-R102 | Back Pressure | V724 | 25 | FC | Ferric Chloride | 300 | 25
Ferric Chloride Application Point for bioreactor 2 | PCV-R1159 | 1-0102-PPID-R104 | Back Pressure | V724 | 25 | FC | Ferric Chloride | 300 | 25
Ferric Chloride Application Point for bioreactor 3 | PCV-R1259 | 1-0102-PPID-R106 | Back Pressure | V724 | 25 | FC | Ferric Chloride | 300 | 25
FSF Pipe | N/A | 1-0102-PPID-R105 | Air release | V752 | 50 | FSF | Fermented Sludge Filtrate | 80-120
RAS pipe | PCV-R4009 | 1-0102-PPID-R108 | Back Pressure | V724 | 25 | SHC | Sodium Hypochlorite | 300 | 25
RAS Pipe | N/A | 1-0102-PPID-R108 | Air release | V752 | 50 | RAS | Return Activated Sludge | 80-120
RAS Pumps P-S217 and P-S218 outlet pipe | N/A | 1-0102-PPID-R108 | Air release | V752 | 50 | RAS | Return Activated Sludge | 80-120
Instrument Air Cleaning | PCV-R1041-1 | 1-0102-PPID-R109 | Pressure reducing | V710 | 25 | IAS | Instrument Air Supply | 550-650 |  |  | Coordinate with instrument vendor and size accordingly
Instrument Air Cleaning | PCV-R1042-1 | 1-0102-PPID-R109 | Pressure reducing | V710 | 25 | IAS | Instrument Air Supply | 550-650 |  |  | Coordinate with instrument vendor and size accordingly
Instrument Air Cleaning | PCV-R1041-2 | 1-0102-PPID-R109 | Pressure reducing | V710 | 25 | IAS | Instrument Air Supply | 550-650 |  |  | Coordinate with instrument vendor and size accordingly
Instrument Air Cleaning | PCV-R1042-2 | 1-0102-PPID-R109 | Pressure reducing | V710 | 25 | IAS | Instrument Air Supply | 550-650 |  |  | Coordinate with instrument vendor and size accordingly
Instrument Air Cleaning | PCV-R1022 | 1-0102-PPID-R109 | Pressure reducing | V710 | 25 | IAS | Instrument Air Supply | 550-650 |  |  | Coordinate with instrument vendor and size accordingly
Instrument Air Cleaning | PCV-R1032 | 1-0102-PPID-R109 | Pressure reducing | V710 | 25 | IAS | Instrument Air Supply | 550-650 |  |  | Coordinate with instrument vendor and size accordingly
Instrument Air Cleaning | PCV-R1051 | 1-0102-PPID-R109 | Pressure reducing | V710 | 25 | IAS | Instrument Air Supply | 550-650 |  |  | Coordinate with instrument vendor and size accordingly
Instrument Air Cleaning | PCV-R1052 | 1-0102-PPID-R109 | Pressure reducing | V710 | 25 | IAS | Instrument Air Supply | 550-650 |  |  | Coordinate with instrument vendor and size accordingly
Instrument Air Cleaning | PCV-R1141-1 | 1-0102-PPID-R109 | Pressure reducing | V710 | 25 | IAS | Instrument Air Supply | 550-650 |  |  | Coordinate with instrument vendor and size accordingly
Instrument Air Cleaning | PCV-R1142-1 | 1-0102-PPID-R109 | Pressure reducing | V710 | 25 | IAS | Instrument Air Supply | 550-650 |  |  | Coordinate with instrument vendor and size accordingly
Instrument Air Cleaning | PCV-R1141-2 | 1-0102-PPID-R109 | Pressure reducing | V710 | 25 | IAS | Instrument Air Supply | 550-650 |  |  | Coordinate with instrument vendor and size accordingly
Instrument Air Cleaning | PCV-R1142-2 | 1-0102-PPID-R109 | Pressure reducing | V710 | 25 | IAS | Instrument Air Supply | 550-650 |  |  | Coordinate with instrument vendor and size accordingly
Instrument Air Cleaning | PCV-R1122 | 1-0102-PPID-R109 | Pressure reducing | V710 | 25 | IAS | Instrument Air Supply | 550-650 |  |  | Coordinate with instrument vendor and size accordingly
Instrument Air Cleaning | PCV-R1132 | 1-0102-PPID-R109 | Pressure reducing | V710 | 25 | IAS | Instrument Air Supply | 550-650 |  |  | Coordinate with instrument vendor and size accordingly
Instrument Air Cleaning | PCV-R1151 | 1-0102-PPID-R109 | Pressure reducing | V710 | 25 | IAS | Instrument Air Supply | 550-650 |  |  | Coordinate with instrument vendor and size accordingly
Instrument Air Cleaning | PCV-R1152 | 1-0102-PPID-R109 | Pressure reducing | V710 | 25 | IAS | Instrument Air Supply | 550-650 |  |  | Coordinate with instrument vendor and size accordingly
Instrument Air Cleaning | PCV-R1241-1 | 1-0102-PPID-R109 | Pressure reducing | V710 | 25 | IAS | Instrument Air Supply | 550-650 |  |  | Coordinate with instrument vendor and size accordingly
Instrument Air Cleaning | PCV-R1242-1 | 1-0102-PPID-R109 | Pressure reducing | V710 | 25 | IAS | Instrument Air Supply | 550-650 |  |  | Coordinate with instrument vendor and size accordingly
Instrument Air Cleaning | PCV-R1241-2 | 1-0102-PPID-R109 | Pressure reducing | V710 | 25 | IAS | Instrument Air Supply | 550-650 |  |  | Coordinate with instrument vendor and size accordingly
Instrument Air Cleaning | PCV-R1242-2 | 1-0102-PPID-R109 | Pressure reducing | V710 | 25 | IAS | Instrument Air Supply | 550-650 |  |  | Coordinate with instrument vendor and size accordingly
Instrument Air Cleaning | PCV-R1222 | 1-0102-PPID-R109 | Pressure reducing | V710 | 25 | IAS | Instrument Air Supply | 550-650 |  |  | Coordinate with instrument vendor and size accordingly
Instrument Air Cleaning | PCV-R1232 | 1-0102-PPID-R109 | Pressure reducing | V710 | 25 | IAS | Instrument Air Supply | 550-650 |  |  | Coordinate with instrument vendor and size accordingly
Instrument Air Cleaning | PCV-R1251 | 1-0102-PPID-R109 | Pressure reducing | V710 | 25 | IAS | Instrument Air Supply | 550-650 |  |  | Coordinate with instrument vendor and size accordingly
Instrument Air Cleaning | PCV-R1252 | 1-0102-PPID-R109 | Pressure reducing | V710 | 25 | IAS | Instrument Air Supply | 550-650 |  |  | Coordinate with instrument vendor and size accordingly
WAS RDT Feed Pump P-R301 Pressure Relief | PSV-R3019 | 1-0102-PPID-R301 | Pressure relief | V735 | 100 | WAS | Waste Activated Sludge | 340 | 10-40 | 22.2
WAS RDT Feed Pump P-R302 Pressure Relief | PSV-R3029 | 1-0102-PPID-R301 | Pressure relief | V735 | 100 | WAS | Waste Activated Sludge | 340 | 10-40 | 22.2
WAS RDT Feed Pump P-R303 Pressure Relief | PSV-R3039 | 1-0102-PPID-R301 | Pressure relief | V735 | 100 | WAS | Waste Activated Sludge | 340 | 10-40 | 22.2
AREA S - SECONDARY CLARIFIERS
Clarifier 4 RAS Outlet | N/A | 1-0102-PPID-S105 | Air release | V752 | 50 | RAS | Return Activated Sludge | 80-120
Clarifier 5 RAS Outlet | N/A | 1-0102-PPID-S106 | Air release | V752 | 50 | RAS | Return Activated Sludge | 80-120
Seal Water Supply to RAS Pump P-S216 | PCV-S2169 | 1-0102-PPID-S204 | Pressure reducing | V710 | 12 | NPW | Non-Potable Water | 685-750 | 150 | 0.025
Seal Water Supply to RAS Pump P-S217 | PCV-S2179 | 1-0102-PPID-S205 | Pressure reducing | V710 | 12 | NPW | Non-Potable Water | 685-750 | 150 | 0.025
Seal Water Supply to RAS Pump P-S218 | PCV-S2189 | 1-0102-PPID-S205 | Pressure reducing | V710 | 12 | NPW | Non-Potable Water | 685-750 | 150 | 0.025
Seal Water Supply to Scum Pump P-S316 | PCV-S3169 | 1-0102-PPID-S303 | Pressure reducing | V710 | 12 | NPW | Non-Potable Water | 685-750 | 150 | 0.025
Seal Water Supply to Scum Pump P-S317 | PCV-S3179 | 1-0102-PPID-S303 | Pressure reducing | V710 | 12 | NPW | Non-Potable Water | 685-750 | 150 | 0.025
Seal Water Supply to Flushing Water Pump P-S550 | PCV-S5509 | 1-0102-PPID-S506 | Pressure reducing | V710 | 12 | NPW | Non-Potable Water | 685-750 | 150 | 0.025
Sludge Transfer Pump P-S401 Pressure Relief | PSV-S4019 | 1-0102-PPID-S208 | Pressure relief | V735 | 150 | STS | Southend Thickened Sludge | 320-400 | 60
Sludge Transfer Pump P-S402 Pressure Relief | PSV-S4029 | 1-0102-PPID-S208 | Pressure relief | V735 | 150 | STS | Southend Thickened Sludge | 320-401 | 60
Potable water backflow preventer | BFP-S544A | 1-0102-PPID-S504 | RP backflow preventer | V642 | 50 | PW | Potable Water
Potable water backflow preventer | BFP-S544B | 1-0102-PPID-S504 | RP backflow preventer | V642 | 50 | PW | Potable Water
Potable water backflow preventer | BFP-S544C | 1-0102-PPID-S504 | RP backflow preventer | V642 | 50 | PW | Potable Water
Potable water backflow preventer | BFP-S544D | 1-0102-PPID-S504 | RP backflow preventer | V642 | 50 | PW | Potable Water
Sodium Hypochlorite Application | PCV-S5541 | 1-0102-PPID-S507 | Back-Pressure | V722 | 12 | SHC | Sodium Hypochlorite
Instrument Air Supply | PCV-S5409-1 | 1-0102-PPID-S107 | Pressure reducing | V710 | - | IAS | Instrument Air Supply | 550-650 |  |  | Supplied by Package Sampler Vendor
AREA K - HIGH RATE CLARIFIERS
Sodium Hydroxide to HRC Train 1 | PCV-K1107 | 1-0102-PPID-K102 | Back-Pressure | V722 | 25 | SHD | Sodium Hydroxide
Sodium Hydroxide to HRC Train 2 | PCV-K1207 | 1-0102-PPID-K104 | Back-Pressure | V722 | 25 | SHD | Sodium Hydroxide
Ferric Chloride to HRC Train 1 | PCV-K1108 | 1-0102-PPID-K102 | Back-Pressure | V722 | 25 | FC | Ferric Chloride
Ferric Chloride to HRC Train 2 | PCV-K1208 | 1-0102-PPID-K104 | Back-Pressure | V722 | 25 | FC | Ferric Chloride
Sodium Hypochlorite to HRC Train 1 | PCV-K1109 | 1-0102-PPID-K102 | Back-Pressure | V722 | 38 | SHC | Sodium Hypochlorite
Sodium Hypochlorite to HRC Train 2 | PCV-K1209 | 1-0102-PPID-K104 | Back-Pressure | V722 | 38 | SHC | Sodium Hypochlorite
Sodium Hypochlorite to HRC Train 1 Effluent Channel and Maturation Tank 1 | PCV-K1133 | 1-0102-PPID-K103 | Back-Pressure | V722 | 38 | SHC | Sodium Hypochlorite
Sodium Hypochlorite to HRC Train 2 Effluent Channel and Maturation Tank 2 | PCV-K1233 | 1-0102-PPID-K105 | Back-Pressure | V722 | 38 | SHC | Sodium Hypochlorite
Sodium Hydroxide to HRC Effluent Channel | PCV-K1509 | 1-0102-PPID-K106 | Back-Pressure | V722 | 25 | SHD | Sodium Hydroxide
Non-Potable Water to HRC Ballast Addition Skid | PCV-K3109 | 1-0102-PPID-K301 | Pressure reducing | V710 | 50 | NPW | Non-Potable Water |  | 414 | 3.8
Flushing Water Lamella Hose Station for HRC Train 1 | PCV-K1144 | 1-0102-PPID-K103 | Pressure reducing | V710 | 20 | FSW | Flushing Water |  | 345
Flushing Water Lamella Hose Station for HRC Train 2 | PCV-K1244 | 1-0102-PPID-K105 | Pressure reducing | V710 | 20 | FSW | Flushing Water |  | 345
AREA D - FERMENTERS / THICKENERS
Fermenters
Seal Water Supply to Fermenter Recirculation Pump P-D321 | PCV-D3219 | 1-0102-PPID-D303 | Pressure reducing | V710 | 12 | NPW | Non-Potable Water | 685-750 | 150 | 0.025
Seal Water Supply to Fermenter Recirculation Pump P-D322 | PCV-D3229 | 1-0102-PPID-D303 | Pressure reducing | V710 | 12 | NPW | Non-Potable Water | 685-750 | 150 | 0.025
Seal Water Supply to Fermenter Recirculation Pump P-D323 | PCV-D3239 | 1-0102-PPID-D303 | Pressure reducing | V710 | 12 | NPW | Non-Potable Water | 685-750 | 150 | 0.025
Thickeners
Flushing Water to WAS RDT RDT-D403 Inlet Piping | PCV-D404 | 1-0102-PPID-D402 | Pressure reducing | V710 | 38 | FSW | Flushing Water | 685-750 | 50-100 | 3.5
Flushing Water to WAS RDT RDT-D404 Inlet Piping | PCV-D4049 | 1-0102-PPID-D402 | Pressure reducing | V710 | 38 | FSW | Flushing Water | 685-750 | 50-100 | 3.5
Flushing Water to WAS RDT RDT-D403 | PCV-D4038 | 1-0102-PPID-D402 | Pressure reducing | V710 | 38 | FSW | Flushing Water | 965 | TBD | 2.2 | Supplied by RDT vendor
Flushing Water to WAS RDT RDT-D404 | PCV-D4048 | 1-0102-PPID-D402 | Pressure reducing | V710 | 38 | FSW | Flushing Water | 965 | TBD | 2.2 | Supplied by RDT vendor
TWAS Pump P-D405 Pressure Relief | PSV-D4059 | 1-0102-PPID-D403 | Pressure relief | V735 | 100 | TWAS | Thickened Waste Activated Sludge | 1035 | 0-10 | 4.4
TWAS Pump P-D406 Pressure Relief | PSV-D4069 | 1-0102-PPID-D403 | Pressure relief | V735 | 100 | TWAS | Thickened Waste Activated Sludge | 1035 | 0-10 | 4.4
FSL RDT Feed Pump P-D411 Pressure Relief | PSV-D4119 | 1-0102-PPID-D404 | Pressure relief | V735 | 100 | FSL | Fermented Sludge | 360 | 20-60 | 22.2
FSL RDT Feed Pump P-D412 Pressure Relief | PSV-D4129 | 1-0102-PPID-D404 | Pressure relief | V735 | 100 | FSL | Fermented Sludge | 360 | 20-60 | 22.2
FSL RDT Feed Pump P-D413 Pressure Relief | PSV-D4139 | 1-0102-PPID-D405 | Pressure relief | V735 | 100 | FSL | Fermented Sludge | 360 | 20-60 | 22.2
FSL RDT Feed Pump P-D414 Pressure Relief | PSV-D4149 | 1-0102-PPID-D405 | Pressure relief | V735 | 100 | FSL | Fermented Sludge | 360 | 20-60 | 22.2
Flushing Water to FSL RDT RDT-D415 Inlet Piping | PCV-D4159 | 1-0102-PPID-D406 | Pressure reducing | V710 | 38 | FSW | Flushing Water | 685-750 | 50-100 | 3.5
Flushing Water to FSL RDT RDT-D416 Inlet Piping | PCV-D4169 | 1-0102-PPID-D406 | Pressure reducing | V710 | 38 | FSW | Flushing Water | 685-750 | 50-100 | 3.5
Flushing Water to FSL RDT RDT-D417 Inlet Piping | PCV-D4179 | 1-0102-PPID-D407 | Pressure reducing | V710 | 38 | FSW | Flushing Water | 685-750 | 50-100 | 3.5
Flushing Water to FSL RDT RDT-D415 | PCV-D4158 | 1-0102-PPID-D406 | Pressure reducing | V710 | 38 | FSW | Flushing Water | 965 | TBD | 2.2 | Supplied by RDT vendor
Flushing Water to FSL RDT RDT-D416 | PCV-D4168 | 1-0102-PPID-D406 | Pressure reducing | V710 | 38 | FSW | Flushing Water | 965 | TBD | 2.2 | Supplied by RDT vendor
Flushing Water to FSL RDT RDT-D417 | PCV-D4178 | 1-0102-PPID-D407 | Pressure reducing | V710 | 38 | FSW | Flushing Water | 965 | TBD | 2.2 | Supplied by RDT vendor
TFS Pump P-D418 Pressure Relief | PSV-D4189 | 1-0102-PPID-D408 | Pressure relief | V735 | 100 | TFS | Thickened Fermented Sludge | 1035 | 0-10 | 9.2
TFS Pump P-D419 Pressure Relief | PSV-D4199 | 1-0102-PPID-D408 | Pressure relief | V735 | 100 | TFS | Thickened Fermented Sludge | 1035 | 0-10 | 9.2
TFS Pump P-D420 Pressure Relief | PSV-D4209 | 1-0102-PPID-D409 | Pressure relief | V735 | 100 | TFS | Thickened Fermented Sludge | 1035 | 0-10 | 9.2
RDT Wash Water Hydropneumatic Tank Pressure Relief | PSV-D4309 | 1-0102-PPID-D410 | Pressure relief | - | TBD | FSW | Flushing Water | TBD | TBD | TBD | Supplied by booster pump vendor
FSF Piping Upstream Flowmeter FE-D4605 | N/A | 1-0102-PPID-D413 | Air release | V752 | 50 | FSF | Fermented Sludge Filtrate | 30-50
FSF Piping Downstream Flowmeter FE-D4605 | N/A | 1-0102-PPID-D413 | Air release | V752 | 50 | FSF | Fermented Sludge Filtrate | 30-50
AREA T - BIOFILTER / ODOUR CONTROL
Biofilter Cell 1 | ARV-T2101 | 1-0102-PPID-T201 | Vacuum | V738 | 300 | FOA | Foul Air |  |  |  | Factory set at 5000 Pascals vacuum
Biofilter Cell 2 | ARV-T2201 | 1-0102-PPID-T202 | Vacuum | V738 | 300 | FOA | Foul Air |  |  |  | Factory set at 5000 Pascals vacuum
Biofilter Cell 3 | ARV-T2301 | 1-0102-PPID-T203 | Vacuum | V738 | 300 | FOA | Foul Air |  |  |  | Factory set at 5000 Pascals vacuum
Glycol Recirculation Pumps Loop Vent | ARV-T1059 | 1-0102-PPID-T102 | Air release | V752 |  | GS | Glycol Supply |  |  |  | Supplied by Biofilter vendor
Natural Gas Supply | PCV-T1069-1 | 1-0102-PPID-T102 | Pressure Regulator | - | 32 | NG | Natural Gas | - | - | - | Supplied by Biofilter vendor
Natural Gas Supply | PCV-T1069-2 | 1-0102-PPID-T102 | Pressure Regulator | - | 32 | NG | Natural Gas | - | - | - | Supplied by Biofilter vendor
Natural Gas Pressure Relief | PRV-T1069-1 | 1-0102-PPID-T102 | Pressure Relief | - | 25 | NG | Natural Gas | - | - | - | Supplied by Biofilter vendor
Natural Gas Pressure Relief | PRV-T1069-2 | 1-0102-PPID-T102 | Pressure Relief | - | 25 | NG | Natural Gas | - | - | - | Supplied by Biofilter vendor
Biofilter Heater Coil Glycol Recirculation | PRV-T1059 | 1-0102-PPID-T102 | Pressure Relief | - | 25 | GS | Glycol Supply | - | - | - | Supplied by Biofilter vendor
NPW Supply to Biolfilters | PRV-T1409 | 1-0102-PPID-T107 | Pressure Reducing | V710 | 38 | NPW | Non-Potable Water | 685-750 | 150 | 2.5
AREA C - CHEMICAL BUILDING / ELECTRICAL BUILDING
Flushing water | PCV-C4169 | 1-0102-PPID-C402 | Pressure reducing | V710 | 75 | FSW | Flushing Water | 685-750 | 150-350
Flushing water | PCV-C4179 | 1-0102-PPID-C403 | Pressure reducing | V710 | 75 | FSW | Flushing Water | 685-750 | 150-350
Flushing water | PCV-C4189 | 1-0102-PPID-C404 | Pressure reducing | V710 | 75 | FSW | Flushing Water | 685-750 | 150-350
Flushing water | PCV-C4369 | 1-0102-PPID-C406 | Pressure reducing | V710 | 75 | FSW | Flushing Water | 685-750 | 150-350
Flushing water | PCV-C4379 | 1-0102-PPID-C407 | Pressure reducing | V710 | 75 | FSW | Flushing Water | 685-750 | 150-350
Flushing water | PCV-C4569 | 1-0102-PPID-C409 | Pressure reducing | V710 | 75 | FSW | Flushing Water | 685-750 | 150-350
Flushing water | PCV-C4579 | 1-0102-PPID-C410 | Pressure reducing | V710 | 75 | FSW | Flushing Water | 685-750 | 150-350
Flushing water | PCV-C4762 | 1-0102-PPID-C412 | Pressure reducing | V710 | 75 | FSW | Flushing Water | 685-750 | 150-350
Potable water backflow preventer | BFP-C530K | 1-0102-PPID-C503 | RP backflow preventer | V642 | 100 | PW | Potable Water
Potable water backflow preventer | BFP-C530L | 1-0102-PPID-C503 | RP backflow preventer | V642 | 100 | PW | Potable Water
Potable water backflow preventer | BFP-C530M | 1-0102-PPID-C503 | RP backflow preventer | V642 | 100 | PW | Potable Water
Potable water backflow preventer | BFP-C530N | 1-0102-PPID-C503 | RP backflow preventer | V642 | 100 | PW | Potable Water
Potable water backflow preventer | BFP-C510D | 1-0102-PPID-C503 | RP backflow preventer | V642 | 32 | DHW | Domestic Hot Water
Potable water backflow preventer | BFP-C510E | 1-0102-PPID-C503 | RP backflow preventer | V642 | 32 | DHW | Domestic Hot Water
Bioreactor Ferric Chloride Pump P-C111 Pressure Relief Valve | PSV-C1119 | 1-0102-PPID-C102 | Pressure relief | - | - | FC | Ferric Chloride | - | - | - | Supplied by chemical pump skid supplier
Bioreactor Ferric Chloride Pump P-C112 Pressure Relief Valve | PSV-C1129 | 1-0102-PPID-C102 | Pressure relief | - | - | FC | Ferric Chloride | - | - | - | Supplied by chemical pump skid supplier
Bioreactor Ferric Chloride Pump P-C113 Pressure Relief Valve | PSV-C1139 | 1-0102-PPID-C102 | Pressure relief | - | - | FC | Ferric Chloride | - | - | - | Supplied by chemical pump skid supplier
Bioreactor Ferric Chloride Pump P-C114 Pressure Relief Valve | PSV-C1149 | 1-0102-PPID-C103 | Pressure relief | - | - | FC | Ferric Chloride | - | - | - | Supplied by chemical pump skid supplier
Bioreactor Ferric Chloride Pump P-C115 Pressure Relief Valve | PSV-C1159 | 1-0102-PPID-C103 | Pressure relief | - | - | FC | Ferric Chloride | - | - | - | Supplied by chemical pump skid supplier
Bioreactor Ferric Chloride Pump P-C116 Pressure Relief Valve | PSV-C1169 | 1-0102-PPID-C103 | Pressure relief | - | - | FC | Ferric Chloride | - | - | - | Supplied by chemical pump skid supplier
HRC Ferric Chloride Pump P-C121 Pressure Relief Valve | PSV-C1219 | 1-0102-PPID-C104 | Pressure relief | - | - | FC | Ferric Chloride | - | - | - | Supplied by chemical pump skid supplier
HRC Ferric Chloride Pump P-C122 Pressure Relief Valve | PSV-C1229 | 1-0102-PPID-C104 | Pressure relief | - | - | FC | Ferric Chloride | - | - | - | Supplied by chemical pump skid supplier
HRC Ferric Chloride Pump P-C123 Pressure Relief Valve | PSV-C1239 | 1-0102-PPID-C104 | Pressure relief | - | - | FC | Ferric Chloride | - | - | - | Supplied by chemical pump skid supplier
HRC Ferric Chloride Pump P-C131 Pressure Relief Valve | PSV-C1319 | 1-0102-PPID-C105 | Pressure relief | - | - | FC | Ferric Chloride | - | - | - | Supplied by chemical pump skid supplier
HRC Ferric Chloride Pump P-C132 Pressure Relief Valve | PSV-C1329 | 1-0102-PPID-C105 | Pressure relief | - | - | FC | Ferric Chloride | - | - | - | Supplied by chemical pump skid supplier
HRC Ferric Chloride Pump P-C133 Pressure Relief Valve | PSV-C1339 | 1-0102-PPID-C105 | Pressure relief | - | - | FC | Ferric Chloride | - | - | - | Supplied by chemical pump skid supplier
Sodium Hydroxide Pump P-C231 Pressure Relief Valve | PSV-C2319 | 1-0102-PPID-C202 | Pressure relief | - | - | SHD | Sodium Hydroxide | - | - | - | Supplied by chemical pump skid supplier
Sodium Hydroxide Pump P-C232 Pressure Relief Valve | PSV-C2329 | 1-0102-PPID-C202 | Pressure relief | - | - | SHD | Sodium Hydroxide | - | - | - | Supplied by chemical pump skid supplier
Sodium Hypochlorite Pump P-C241 Pressure Relief Valve | PSV-C2419 | 1-0102-PPID-C203 | Pressure relief | - | - | SHC | Sodium Hypochlorite | - | - | - | Supplied by chemical pump skid supplier
Sodium Hypochlorite Pump P-C242 Pressure Relief Valve | PSV-C2429 | 1-0102-PPID-C203 | Pressure relief | - | - | SHC | Sodium Hypochlorite | - | - | - | Supplied by chemical pump skid supplier
Sodium Hypochlorite Pump P-C211 Pressure Relief Valve | PSV-C2119 | 1-0102-PPID-C204 | Pressure relief | - | - | SHC | Sodium Hypochlorite | - | - | - | Supplied by chemical pump skid supplier
Sodium Hypochlorite Pump P-C212 Pressure Relief Valve | PSV-C2129 | 1-0102-PPID-C204 | Pressure relief | - | - | SHC | Sodium Hypochlorite | - | - | - | Supplied by chemical pump skid supplier
Sodium Hypochlorite Pump P-C221 Pressure Relief Valve | PSV-C2219 | 1-0102-PPID-C205 | Pressure relief | - | - | SHC | Sodium Hypochlorite | - | - | - | Supplied by chemical pump skid supplier
Sodium Hypochlorite Pump P-C222 Pressure Relief Valve | PSV-C2229 | 1-0102-PPID-C205 | Pressure relief | - | - | SHC | Sodium Hypochlorite | - | - | - | Supplied by chemical pump skid supplier
Sodium Hypochlorite Pump P-C223 Pressure Relief Valve | PSV-C2239 | 1-0102-PPID-C205 | Pressure relief | - | - | SHC | Sodium Hypochlorite | - | - | - | Supplied by chemical pump skid supplier
Sodium Bisulphite Pump P-C311 Pressure Relief Valve | PSV-C3119 | 1-0102-PPID-C301 | Pressure relief | - | - | SBS | Sodium Bisulphite | - | - | - | Supplied by chemical pump skid supplier
Sodium Bisulphite Pump P-C312 Pressure Relief Valve | PSV-C3129 | 1-0102-PPID-C301 | Pressure relief | - | - | SBS | Sodium Bisulphite | - | - | - | Supplied by chemical pump skid supplier
Carrier water for SBS service | PCV-C3109 | 1-0102-PPID-C301 | Pressure reducing | V710 | 50 | FSW | Flushing Water | 685-750 | 150-350
FSL RDT Post Dilution Polymer Pump P-C411 Pressure Relief Valve | PSV-C4119 | 1-0102-PPID-C402 | Pressure relief | - | - | MP | Mixed Polymer | - | - | - | Supplied by chemical pump skid supplier
FSL RDT Post Dilution Polymer Pump P-C412 Pressure Relief Valve | PSV-C4129 | 1-0102-PPID-C402 | Pressure relief | - | - | MP | Mixed Polymer | - | - | - | Supplied by chemical pump skid supplier
FSL RDT Post Dilution Polymer Pump P-C413 Pressure Relief Valve | PSV-C4139 | 1-0102-PPID-C403 | Pressure relief | - | - | MP | Mixed Polymer | - | - | - | Supplied by chemical pump skid supplier
FSL RDT Post Dilution Polymer Pump P-C414 Pressure Relief Valve | PSV-C4149 | 1-0102-PPID-C403 | Pressure relief | - | - | MP | Mixed Polymer | - | - | - | Supplied by chemical pump skid supplier
FSL RDT Post Dilution Polymer Pump P-C415 Pressure Relief Valve | PSV-C4159 | 1-0102-PPID-C404 | Pressure relief | - | - | MP | Mixed Polymer | - | - | - | Supplied by chemical pump skid supplier
WAS RDT Post Dilution Polymer Pump P-C431 Pressure Relief Valve | PSV-C4319 | 1-0102-PPID-C406 | Pressure relief | - | - | MP | Mixed Polymer | - | - | - | Supplied by chemical pump skid supplier
WAS RDT Post Dilution Polymer Pump P-C432 Pressure Relief Valve | PSV-C4329 | 1-0102-PPID-C406 | Pressure relief | - | - | MP | Mixed Polymer | - | - | - | Supplied by chemical pump skid supplier
WAS RDT Post Dilution Polymer Pump P-C433 Pressure Relief Valve | PSV-C4339 | 1-0102-PPID-C407 | Pressure relief | - | - | MP | Mixed Polymer | - | - | - | Supplied by chemical pump skid supplier
HRC Post Dilution Polymer Pump P-C451 Pressure Relief Valve | PSV-C4519 | 1-0102-PPID-C409 | Pressure relief | - | - | MP | Mixed Polymer | - | - | - | Supplied by chemical pump skid supplier
HRC Post Dilution Polymer Pump P-C452 Pressure Relief Valve | PSV-C4529 | 1-0102-PPID-C409 | Pressure relief | - | - | MP | Mixed Polymer | - | - | - | Supplied by chemical pump skid supplier
HRC Post Dilution Polymer Pump P-C453 Pressure Relief Valve | PSV-C4359 | 1-0102-PPID-C410 | Pressure relief | - | - | MP | Mixed Polymer | - | - | - | Supplied by chemical pump skid supplier
Secondary Clarifier Post Dilution Polymer Pump P-C471 Pressure Relief Valve | PSV-C4719 | 1-0102-PPID-C412 | Pressure relief | - | - | MP | Mixed Polymer | - | - | - | Supplied by chemical pump skid supplier
Secondary Clarifier Post Dilution Polymer Pump P-C472 Pressure Relief Valve | PSV-C4729 | 1-0102-PPID-C412 | Pressure relief | - | - | MP | Mixed Polymer | - | - | - | Supplied by chemical pump skid supplier
Sodium Hydroxide Pump P-C231 Pressure Regulating Valve | PCV-C2319 | 1-0102-PPID-C202 | Pressure Regulator | - | - | SHD | Sodium Hydroxide | - | - | - | Supplied by chemical pump skid supplier
Sodium Hydroxide Pump P-C232 Pressure Regulating Valve | PCV-C2329 | 1-0102-PPID-C202 | Pressure Regulator | - | - | SHD | Sodium Hydroxide | - | - | - | Supplied by chemical pump skid supplier
Sodium Hypochlorite Pump P-C241 Pressure Regulating Valve | PCV-C2419 | 1-0102-PPID-C203 | Pressure Regulator | - | - | SHC | Sodium Hypochlorite | - | - | - | Supplied by chemical pump skid supplier
Sodium Hypochlorite Pump P-C242 Pressure Regulating Valve | PCV-C2429 | 1-0102-PPID-C203 | Pressure Regulator | - | - | SHC | Sodium Hypochlorite | - | - | - | Supplied by chemical pump skid supplier
Sodium Hypochlorite Pump P-C211 Pressure Regulating Valve | PCV-C2119 | 1-0102-PPID-C204 | Pressure Regulator | - | - | SHC | Sodium Hypochlorite | - | - | - | Supplied by chemical pump skid supplier
Sodium Hypochlorite Pump P-C212 Pressure Regulating Valve | PCV-C2129 | 1-0102-PPID-C204 | Pressure Regulator | - | - | SHC | Sodium Hypochlorite | - | - | - | Supplied by chemical pump skid supplier
Sodium Hypochlorite Pump P-C221 Pressure Regulating Valve | PCV-C2219 | 1-0102-PPID-C205 | Pressure Regulator | - | - | SHC | Sodium Hypochlorite | - | - | - | Supplied by chemical pump skid supplier
Sodium Hypochlorite Pump P-C222 Pressure Regulating Valve | PCV-C2229 | 1-0102-PPID-C205 | Pressure Regulator | - | - | SHC | Sodium Hypochlorite | - | - | - | Supplied by chemical pump skid supplier
Sodium Hypochlorite Pump P-C223 Pressure Regulating Valve | PCV-C2239 | 1-0102-PPID-C205 | Pressure Regulator | - | - | SHC | Sodium Hypochlorite | - | - | - | Supplied by chemical pump skid supplier
Sodium Bisulphite Pump P-C311 Pressure Regulating Valve | PCV-C3119 | 1-0102-PPID-C301 | Pressure Regulator | - | - | SBS | Sodium Bisulphite | - | - | - | Supplied by chemical pump skid supplier
Sodium Bisulphite Pump P-C312 Pressure Regulating Valve | PCV-C3129 | 1-0102-PPID-C301 | Pressure Regulator | - | - | SBS | Sodium Bisulphite | - | - | - | Supplied by chemical pump skid supplier
BUILDING MECHANICAL
AREA G - HEADWORKS
AREA P - PRIMARY CLARIFIERS
AREA G - HEADWORKS
Flushing Water to glycol heat recovery | PCV-G6739-1 | 1-0102-PPID-G623 | Pressure reducing | V716 | 100 | FSW | Flushing Water | 685-750 | 150-350
Flushing Water to glycol heat recovery | PCV-G6739-2 | 1-0102-PPID-G623 | Pressure reducing | V716 | 100 | FSW | Flushing Water | 685-750 | 150-350
AREA R - BIOREACTORS / BLOWER BUILDING
Natural Gas to Air Handling Unit AHU-R610 | PCV-R6109 | 1-0102-PPID-R603 | Pressure Reducing | V754 | 32 | NG | Natural Gas | 34.4 | 2
Natural Gas to Unit Heater GUH-R654 | PCV-R6541 | 1-0102-PPID-R608 | Pressure Reducing | V754 | 12 | NG | Natural Gas | 34.4 | 2
Natural Gas to Unit Heater GUH-R624 | PCV-R6249 | 1-0102-PPID-R607 | Pressure Reducing | V754 | 12 | NG | Natural Gas | 34.4 | 2
Natural Gas to Unit Heater GUH-R625 | PCV-R6259 | 1-0102-PPID-R607 | Pressure Reducing | V754 | 12 | NG | Natural Gas | 34.4 | 2
AREA S - SECONDARY CLARIFIERS
Natural Gas to Air Handling Unit AHU-S630 | PCV-S6309 | 1-0102-PPID-S622 | Pressure Reducing | V754 | 38 | NG | Natural Gas | 34.4 | 2
Natural Gas to Air Handling Unit AHU-S650 | PCV-S6509 | 1-0102-PPID-S623 | Pressure Reducing | V754 | 38 | NG | Natural Gas | 34.4 | 2
Natural Gas to Unit Heater UH-S655 | PCV-S6559 | 1-0102-PPID-S626 | Pressure Reducing | V754 | 12 | NG | Natural Gas | 34.4 | 2
Natural Gas to Unit Heater UH-S656 | PCV-S6569 | 1-0102-PPID-S626 | Pressure Reducing | V754 | 12 | NG | Natural Gas | 34.4 | 2
Natural Gas to Unit Heater UH-S659 | PCV-S6599 | 1-0102-PPID-S626 | Pressure Reducing | V754 | 12 | NG | Natural Gas | 34.4 | 2
Flushing water pressure reducing valve | PCV-S6639 | 1-0102-PPID-S627 | Pressure Reducing | V716 | 100 | FSW | Flushing Water
AREA U - UV DISINFECTION BUILDING
Natural Gas to Air Handling Unit AHU-U640 | PCV-U6409 | 1-0102-PPID-U601 | Pressure Reducing | V754 | 25 | NG | Natural Gas | 34.4 | 2
Natural Gas to Unit Heater UH-U650 | PCV-U6509 | 1-0102-PPID-U602 | Pressure Reducing | V754 | 12 | NG | Natural Gas | 34.4 | 2
Natural Gas to Unit Heater UH-U651 | PCV-U6519 | 1-0102-PPID-U602 | Pressure Reducing | V754 | 12 | NG | Natural Gas | 34.4 | 2
Natural Gas to Unit Heater UH-U652 | PCV-U6529 | 1-0102-PPID-U602 | Pressure Reducing | V754 | 12 | NG | Natural Gas | 34.4 | 2
Natural Gas to Unit Heater UH-U654 | PCV-U6549 | 1-0102-PPID-U602 | Pressure Reducing | V754 | 12 | NG | Natural Gas | 34.4 | 2
AREA K - HIGH RATE CLARIFIERS
AREA D - FERMENTERS / THICKENERS
Natural Gas to Air Handling Unit AHU-D610 | PCV-D6109 | 1-0102-PPID-D601 | Pressure Reducing | V754 | 50 | NG | Natural Gas | 34.4 | 2
Natural Gas to Air Handling Unit AHU-D620 | PCV-D6209 | 1-0102-PPID-D602 | Pressure Reducing | V754 | 25 | NG | Natural Gas | 34.4 | 2
AREA T - BIOFILTER / ODOUR CONTROL
Odour Control Biofilter TK--T210 |  | 1-0102-PPID-T201 | Vacuum Relief | V738 | 300 | FOA | Foul Air |  |  |  | Set at minus 5000 Pascals
Odour Control Biofilter TK--T220 |  | 1-0102-PPID-T201 | Vacuum Relief | V738 | 300 | FOA | Foul Air |  |  |  | Set at minus 5000 Pascals
Odour Control Biofilter TK--T230 |  | 1-0102-PPID-T201 | Vacuum Relief | V738 | 300 | FOA | Foul Air |  |  |  | Set at minus 5000 Pascals
Natural gas to AHU gas burner | PCV-T6109 | 1-0102-PPID-T601 | Pressure reducing | V754 | 32 | NG | Natural Gas | 34.4 | 2
AREA C - CHEMICAL BUILDING / ELECTRICAL BUILDING
Natural gas to gas water heater | PCV-C5309-1 | 1-0102-PPID-C503 | Pressure reducing | V754 | 32 | NG | Natural Gas | 34.4 | 2
Natural gas to gas water heater | PCV-C5309-2 | 1-0102-PPID-C503 | Pressure reducing | V754 | 32 | NG | Natural Gas | 34.4 | 2
Natural gas to gas water heater | PCV-C5309-3 | 1-0102-PPID-C503 | Pressure reducing | V754 | 32 | NG | Natural Gas | 34.4 | 2
Non-potable Water | PCV-C5109 | 1-0102-PPID-C504 | Pressure reducing | V716 | 100 | NPW | Non-Potable Water | 685-750 | 150-350
Natural gas to AHU gas burner | PCV-C6119 | 1-0102-PPID-C601 | Pressure reducing | V754 | 32 | NG | Natural Gas | 34.4 | 2
Natural gas to AHU gas burner | PCV-C6129 | 1-0102-PPID-C602 | Pressure reducing | V754 | 32 | NG | Natural Gas | 34.4 | 2
Natural gas to AHU gas burner | PCV-C6209 | 1-0102-PPID-C603 | Pressure reducing | V754 | 32 | NG | Natural Gas | 34.4 | 2
Natural gas to Heater Unit | PCV-C6179 | 1-0102-PPID-C607 | Pressure reducing | V754 | 12 | NG | Natural Gas | 34.4 | 2
Natural gas to Heater Unit | PCV-C6639 | 1-0102-PPID-C608 | Pressure reducing | V754 | 12 | NG | Natural Gas | 34.4 | 2
Natural gas to Heater Unit | PCV-C6649 | 1-0102-PPID-C608 | Pressure reducing | V754 | 12 | NG | Natural Gas | 34.4 | 2
Potable water pressure reducing | PCV-C5309 | 1-0102-PPID-C503 | Pressure reducing | V710 | 50 | PW | Potable Water
AREA Y - YARD / ELECTRICAL SUBSTATION
AREA B - SERVICE BUILDING
AREA M - ADMINISTRATION BUILDING
General Notes:
1. This schedule is provided for the Contractor's convenience and shall not be taken as complete.
2. Valves to be supplied and installed under this contract unless otherwise indicated.
3. n/a = not applicable; valve supplied by others, installed under this contract.
4. Refer to the scope of pre-purchased equipment for valves that are supplied by others to be installed under this contract.
Notes:
1. Inlet Pressure = Set pressure for pressure relief valve or upstream pressure for pressure reducing valve.
Bottom of print range

## Commodity Codes (hidden)
ALP | Air, Low Pressure
BLS | Ballasted Sludge
CA | Compressed Air
CDR | Condenser Water Return
CDS | Condenser Water Supply
CE | Centrate
CG | Calibration Gas
CHR | Chilled Water Return
CHS | Chilled Water Supply
CL2 | Chlorine
CO2 | Carbon Dioxide
CON | Condensate
CS | Combined Sewer
CWR | Cooling Water Return
CWS | Cooling Water Supply
D | Drain (non-process)
DFR | Diesel Fuel Return
DFS | Diesel Fuel Supply
DHR | Domestic Hot Water Return
DG | Digester Gas
DGH | Digester Gas, High Pressure
DHW | Domestic Hot Water
DL | Decant Liquor
DP | Dry Polymer
DS | Digester Sludge
EA | Exhaust Air
ES | Electrical Supply
FC | Ferric Chloride
FE | Final Effluent
FOA | Foul Air
FPW | Fire Protection Water
FSF | Fermented Sludge Filtrate
FSL | Fermented Sludge
FSU | Fermenter Supernatent
FSW | Flushing Water
GE | Grit Effluent
GR | Glycol Return
GRS | Grit Slurry
GRT | Grit (solids)
GS | Glycol Supply
HCO | Hydraulic Oil
HFW | Hot Flushing Water
HRS | High Rate Clarifier Sludge
HWR | Hot Water Return
HWS | Hot Water Supply
H2 | Hydrogen
IAS | Instrument Air Supply
LCP | Liquid Concentrated Polymer
LDS | Land Drainage Sewer
LGO | Lubricating Oil
LOX | Liquid Oxygen
LPS | Low Pressure Steam
MA | Mixed Air
MET | Methanol
ML | Mixed Liquor
MP | Mixed Polymer
N2 | Nitrogen Gas
N2L | Nitrogen Liquid
NG | Natural Gas
NPH | Non-Potable Hot Water
NPT | Non-Potable Tempered Water
NPW | Non-Potable Water
OA | Outdoor Air
O2 | Oxygen Gas
PD | Process Drain
PE | Primary Effluent
PO | Process Overflow
PS | Primary Sludge
PV | Process Vent
PW | Potable Water
R | Refrigerant
RA | Return Air
RAS | Return Activated Sludge
RS | Raw Sewage
RW | Rain/Roof Water
SA | Supply Air
SAM | Sample
SBS | Sodium Bisulphite
SC | Scum
SCB | Sodium Carbonate (soda ash)
SCS | Screenings
SE | Secondary Effluent
SEA | Service Air
SHC | Sodium Hypochlorite
SHD | Sodium Hydroxide
SLC | Sludge Cake
SND | Sand (solid)
SNS | Sand Slurry
SPD | Sump Pump Discharge
SRS | Storm Relief Sewer
STS | Southend Thickened Sludge
SUB | DAF Subnatent
TBS | Thickened Bottom Sludge
TCE | Treated Centrate
TDW | Tempered Domestic Water
TFS | Thickened Fermented Sludge
TO | Thermal Oxidizer
TS | Thin Sludge
TWAS | Thickened Waste Activated Sludge
VAC | Vacuum
VTA | Vent to Atmosphere
W | Water
WA | Waste Air
WAS | Waste Activated Sludge
WSF | Waste Activated Sludge Filtrate
WWS | Wastewater Sewer
Various | Various