## Yard Potential Ground
OWAM - CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Visual inspection of the grounding test well. |  |  |  | 0
Inspect exposed grounding to ensure nothing is loose and no corrosion. |  |  |  | 0
Test the grounding test well. |  |  |  | 0
Perform point-to-point tests to determine the resistance between the main grounding system and all major electrical equiptment frames, system neutral, and/or derived neutral points. |  |  |  | 0

## DS-E7013
OWAM - CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Perform visual inspections for any damages and clean insulators. |  |  |  | 0
Perform IR scan for any hot spots. |  |  |  | 0
Perform contact resistance test. |  |  |  | 0
Perform bolted connection resistance test. |  |  |  | 0
Perform visual inspections for any sign of corona, tracking, and thermal damages. |  |  |  | 0
Perform overportential test. |  |  |  | 0
Check kirk key operation |  |  |  | 0
Perform visual inspection for switch alignment while manually operating the disconnect. |  |  |  | 0
Exercise the disconnect. |  |  |  | 0
Check for loose connection and any cracks. |  |  |  | 0
Check the proper operation of auxiliary switches and control box heater. |  |  |  | 0
Check that the nameplate data matches the drawings. |  |  |  | 0
Check drive linkage and operating assembly and lubricate as required. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0

## CB-E7013
OWAM - CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Visual inspection for any broken parts. Clean and lubricate all mechanical linkages. |  |  |  | 0
Check all control wirings and associated fitted components. |  |  |  | 0
Check mechanical operations. |  |  |  | 0
Check the operation of the heaters for the tank. |  |  |  | 0
Check if there is any leak on the tank using SF6 sniffer device. |  |  |  | 0
Record the breaker operation counter reading. |  |  |  | 0
Verify/test gas pressure switch setting (SW1 to SW3) and the 63X function and alarms. |  |  |  | 0
Clean insulators. |  |  |  | 0
Check interrupter pressure relief plates. |  |  |  | 0
Check functionality of kirk key interlock an emergency trip button. |  |  |  | 0
Perform contact resistance test and dynamic resistance measurment. |  |  |  | 0
Perform breaker timing test. |  |  |  | 0
Visually inspect the internal condition of breaker control panel. Ensure all components are working properly. |  |  |  | 0
Perform breaker motion analysis test. |  |  |  | 0
Perform breaker control functional test including alarms, pressure switches, limit switches, etc. |  |  |  | 0
Perform power factor or dissipation factor test on each pole and bushing. |  |  |  | 0
Check for any sign of corona, tracking, ad thermal damages. |  |  |  | 0
Perform breaker trip test (manually and automatically). Visually check the condition of the breaker. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0

## TVSS-E7013-1
OWAM - CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Check for physical damage such as cracks, chips, or corrosion. |  |  |  | 0
Check the torque on all bolts. Tighten as required. |  |  |  | 0
Check the proper rating of the arresters. |  |  |  | 0
Perform insulation resistance/ doble test for leakage current. |  |  |  | 0
Verify that each surge arrester ground lead is individually attached to a ground bus or ground electrode. |  |  |  | 0
Perform bolted connection resistance test. |  |  |  | 0
Clean arrester sheds. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0

## PT-E7013
OWAM - CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Check the condition of PT. Check for any physical damages. |  |  |  | 0
Check the grounding connection. |  |  |  | 0
Check the elibibility of the name plate. |  |  |  | 0
Tighten any loose connection. |  |  |  | 0
Check the fuse condition and verify the size. |  |  |  | 0
Perform IR scan for hot spots. |  |  |  | 0
Perform insulation resistance test. |  |  |  | 0
Perform turns ratio test. |  |  |  | 0
Clean PT as required. |  |  |  | 0
Test oil sample and complete DGA analysis (including H2, C2H2, C2H4, CO, and CH4). |  |  |  | 0
Measure capacitance and dissipation factor and record the finding. |  |  |  | 0
Check for oil leak, read and record pressure gauge reading |  |  |  | 0
Check protective gap. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0

## CT-E7013-A-1
OWAM - CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Conduct visual inspection for any damage. |  |  |  | 0
Perform insulation resistance test of the CT. |  |  |  | 0
Perform thermal (IR) scan. |  |  |  | 0
Tighten any loose connection and check and visible damages. |  |  |  | 0
Clean CT as required. |  |  |  | 0
Perform polarity test. |  |  |  | 0
Perform turn ratio test. |  |  |  | 0
Perform winding resistance test. |  |  |  | 0
Perform excitation test. |  |  |  | 0
Perform burden test. |  |  |  | 0
Check the condition of the nameplate. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0

## CT-E7013-B-1
OWAM - CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Conduct visual inspection for any damage. |  |  |  | 0
Perform insulation resistance test of the CT. |  |  |  | 0
Perform thermal (IR) scan. |  |  |  | 0
Tighten any loose connection and check and visible damages. |  |  |  | 0
Clean CT as required. |  |  |  | 0
Perform polarity test. |  |  |  | 0
Perform turn ratio test. |  |  |  | 0
Perform winding resistance test. |  |  |  | 0
Perform excitation test. |  |  |  | 0
Perform burden test. |  |  |  | 0
Check the condition of the nameplate. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0

## Spare CT
OWAM - CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Conduct visual inspection for any damage. |  |  |  | 0
Perform insulation resistance test of the CT. |  |  |  | 0
Perform thermal (IR) scan. |  |  |  | 0
Tighten any loose connection and check and visible damages. |  |  |  | 0
Clean CT as required. |  |  |  | 0
Perform polarity test. |  |  |  | 0
Perform turn ratio test. |  |  |  | 0
Perform winding resistance test. |  |  |  | 0
Perform excitation test. |  |  |  | 0
Perform burden test. |  |  |  | 0
Check the condition of the nameplate. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0

## Spare CT-1
OWAM - CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Conduct visual inspection for any damage. |  |  |  | 0
Perform insulation resistnace test of the CT. |  |  |  | 0
Perform thermal (IR) scan. |  |  |  | 0
Tighten any loose connection and check and visible damages. |  |  |  | 0
Clean CT as required. |  |  |  | 0
Perform polarity test. |  |  |  | 0
Perform turn ratio test. |  |  |  | 0
Perform winding resistance test. |  |  |  | 0
Perform excitation test. |  |  |  | 0
Perform burden test. |  |  |  | 0
Check the condition of the nameplate. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0

## TVSS-E7013-2
OWAM - CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Check for physical damage such as cracks, chips, or corrosion. |  |  |  | 0
Check the torque on all bolts. Tighten as required. |  |  |  | 0
Check the proper rating of the arresters. |  |  |  | 0
Perform insulation resistance/ doble test for leakage current. |  |  |  | 0
Verify that each surge arrester ground lead is individually attached to a ground bus or ground electrode. |  |  |  | 0
Perform bolted connection resistance test. |  |  |  | 0
Clean arrester sheds. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0

## CT-E7013-B-3
OWAM- CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Conduct visual inspection for any damage. |  |  |  | 0
Perform insulation resistance test of the CT. |  |  |  | 0
Perform thermal (IR) scan. |  |  |  | 0
Tighten any loose connection and check and visible damages. |  |  |  | 0
Clean CT as required. |  |  |  | 0
Perform polarity test. |  |  |  | 0
Perform turn ratio test. |  |  |  | 0
Perform winding resistance test. |  |  |  | 0
Perform excitation test. |  |  |  | 0
Perform burden test. |  |  |  | 0
Check the condition of the nameplate. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0

## CT-E7013-A-3
OWAM- CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Conduct visual inspection for any damage. |  |  |  | 0
Perform insulation resistance test of the CT. |  |  |  | 0
Perform thermal (IR) scan. |  |  |  | 0
Tighten any loose connection and check and visible damages. |  |  |  | 0
Clean CT as required. |  |  |  | 0
Perform polarity test. |  |  |  | 0
Perform turn ratio test. |  |  |  | 0
Perform winding resistance test. |  |  |  | 0
Perform excitation test. |  |  |  | 0
Perform burden test. |  |  |  | 0
Check the condition of the nameplate. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0

## XFMR-E7013
OWAM - CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Check the condition of the bushings, the capacitance and PF value against the nameplate. |  |  |  | 0
Check the operation of cooling fans. |  |  |  | 0
Perform a visual inspection of insulators for evidence of contamination or flashover |  |  |  | 0
Test the oil sample for dielectric strength and water content. |  |  |  | 0
Test oil sample for complete DGA (including H2, C2H2, C2H4, CO, and CH4). |  |  |  | 0
Check DGA monitor (Calisto 2) for hydrogen, moisture, and CO. |  |  |  | 0
Download the databank and event log of the DGA monitor (Calisto 2) and send them to Morgan Schaffer for evaluation of the monitor. |  |  |  | 0
Check for any corrosion, paint chips, and other damages around the transformer. |  |  |  | 0
Perform visual inspection for insulators for evidence of contamination or flashover and clean insulators. |  |  |  | 0
Check the control cabinets for any sign of damages. |  |  |  | 0
Check the grounding connections |  |  |  | 0
Conduct inspection inside the OLTC cabinet to ensure everything is functioning properly such as nothing is loose. |  |  |  | 0
Check OLTC cabinet to ensure it has proper oil level. |  |  |  | 0
Check OLTC to ensure the motor is working properly. |  |  |  | 0
Check OLTC to ensure the cabinet heater is working properly. |  |  |  | 0
Check OLTC to ensure the breather is in proper condition. |  |  |  | 0
Check the condition of radiators. |  |  |  | 0
Perform full internal inspection of the control cabinets devices (such as heaters, etc.) including OLTC panel, operating OLTC for full range, performing insulation test, & ratio check. |  |  |  | 0
Perform winding resistance test. |  |  |  | 0
Perform insulation resistance test (PI). |  |  |  | 0
Perform tan δ test. |  |  |  | 0
Perform SFRA. |  |  |  | 0
Perform Power factor test. |  |  |  | 0
Perform turn ratio test. |  |  |  | 0
Clean the bushings. |  |  |  | 0
Perform megger core/ core-ground test. |  |  |  | 0
35. Perform as-left tests and record the findings. |  |  |  | 0

## NGR-E7013
OWAM - CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Conduct visual inspection to the enclosure for any sign of damage. |  |  |  | 0
Keep the NGR clean of accumulated dust or debris. |  |  |  | 0
Disconnect and Isolate the electrical system being grounded through the NGR and open the connection between the system neutral and the Neutral Grounding Resistor. |  |  |  | 0
Conduct a visual inspection of all the parts for any sign of damages. |  |  |  | 0
Check for cracked insulators or busings. |  |  |  | 0
Check the resistive element for continuity. |  |  |  | 0
Check all the internal connections for tightness. |  |  |  | 0
Check the wiring for signs of damage from heat or overloads. |  |  |  | 0
Perform insulation resistance test. |  |  |  | 0
Perform resistance tests. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0

## CT-E7013-1
OWAM - CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Conduct visual inspection for any damage. |  |  |  | 0
Perform insulation resistance test of the CT. |  |  |  | 0
Perform thermal (IR) scan. |  |  |  | 0
Tighten any loose connection and check and visible damages. |  |  |  | 0
Clean CT as required. |  |  |  | 0
Perform polarity test. |  |  |  | 0
Perform turn ratio test. |  |  |  | 0
Perform winding resistance test. |  |  |  | 0
Perform excitation test. |  |  |  | 0
Perform burden test. |  |  |  | 0
Check the condition of the nameplate. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0

## XFMR-E7111
OWAM - CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Inspect all exposed surfaces for evidence of tampering, battered metal, gouges, etc. |  |  |  | 0
Inspect drain cocks, plugs, fuse mountings, and switches for any evidence of insulating liquid seepage around tank-wall gaskets, seals, etc. |  |  |  | 0
Check tank exterior for signs of a leak. |  |  |  | 0
Walk around unit and listen for abnormal noises. |  |  |  | 0
Verify that transformer is not tilted more than 5 degree from horizontal. |  |  |  | 0
Check if there is unusual odors and oil spots around transformer. |  |  |  | 0
Check the operation of vacuum pressure gauge & record the reading. |  |  |  | 0
Check the operation of liquid temp. gauge & record the reading. |  |  |  | 0
Visually inspect the fuses if the fuses are present. |  |  |  | 0
Check for paint chips and eligibility of nameplate. |  |  |  | 0
Check the cable connections. If there are signs of overheating, check for loose connections or discolored spades (paddles). |  |  |  | 0
Check condition of the HV and LV bushings. Observe for any indication of dirt, leakage, breakage, general damage, heat damage or flashover, and clean the bushings. |  |  |  | 0
Check the cubicle Padlock. (if present). |  |  |  | 0
Check for excessive cable weight or stiff cable conductors putting upward or downward pressure on the bushings due to pad settling. |  |  |  | 0
Check the operation of pressure Relief valve and for dirt & debris. |  |  |  | 0
Test oil sample for complete DGA (iincluding H2, C2H2, C2H4, CO, and CH4). |  |  |  | 0
Check ground connection. |  |  |  | 0
Check the operation of winding temp. gauge & record the reading. |  |  |  | 0
Perform turn ratio test. |  |  |  | 0
Perform winding resistance test. |  |  |  | 0
Perform insulation resistance test (PI). |  |  |  | 0
Perform tan δ test. |  |  |  | 0
Perform SFRA. |  |  |  | 0
Check the condition of radiators. |  |  |  | 0
Perform Power Factor test. |  |  |  | 0
Perform megger core/ core-ground test. |  |  |  | 0
Perform full internal inspection of the control cabinets devices (such as heaters, etc.) including LTC panel, operating LTC for full range, performing insulation test, & ratio check. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0

## CT-7111-1
OWAM- CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Conduct visual inspection for any damage. |  |  |  | 0
Perform insulation resistnace test of the CT. |  |  |  | 0
Perform thermal (IR) scan. |  |  |  | 0
Tighten any loose connection and check and visible damages. |  |  |  | 0
Clean CT as required. |  |  |  | 0
Perform polarity test. |  |  |  | 0
Perform turn ratio test. |  |  |  | 0
Perform winding resistance test. |  |  |  | 0
Perform excitation test. |  |  |  | 0
Perform burden test. |  |  |  | 0
Check the condition of the nameplate. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0

## NGR-E7111
OWAM- CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Conduct visual inspection to the enclosure for any sign of damage. |  |  |  | 0
Keep the NGR clean of accumulate dust or debris. |  |  |  | 0
Disconnect and Isolate the electrical system being grounded through the NGR and open the connection between the system neutral and the Neautral Grounding Resistor. |  |  |  | 0
Conduct a visual inspection of all the parts for any sign of damages. |  |  |  | 0
Check for cracked insulators or busings. |  |  |  | 0
Check the resistive element for continuity. |  |  |  | 0
Check all the internal connections for tightness. |  |  |  | 0
Check the wiring for signs of damage from heat or overloads. |  |  |  | 0
Perform insulation resistance test. |  |  |  | 0
Perform resistance tests. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0

## CT-E7111-2
OWAM- CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Conduct visual inspection for any damage. |  |  |  | 0
Perform insulation resistance test of the CT. |  |  |  | 0
Perform thermal (IR) scan. |  |  |  | 0
Tighten any loose connection and check and visible damages. |  |  |  | 0
Clean CT as required. |  |  |  | 0
Perform polarity test. |  |  |  | 0
Perform turn ratio test. |  |  |  | 0
Perform winding resistance test. |  |  |  | 0
Perform excitation test. |  |  |  | 0
Perform burden test. |  |  |  | 0
Check the condition of the nameplate. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0

## DS-E7023
OWAM- CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Perform visual inspections for any damages and clean insulators. |  |  |  | 0
Perform IR scan for any hot spots. |  |  |  | 0
Perform contact resistance test. |  |  |  | 0
Perform bolted connection resistance test |  |  |  | 0
Perform visual inspections for any sign of corona, tracking, and thermal damages. |  |  |  | 0
Perform overportential test. |  |  |  | 0
Check kirk key operation. |  |  |  | 0
Perform visual inspection for switch alignment while manually operating the disconnect. |  |  |  | 0
Exercise the disconnect. |  |  |  | 0
Check for loose connection and any cracks. |  |  |  | 0
Check the proper operation of auxiliary switches and control box heater. |  |  |  | 0
Check that the nameplate data matches the drawings. |  |  |  | 0
Check drive linkage and operating assemly and lubricate as required. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0

## CB-E7023
OWAM- CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Visual inspection for any broken parts. Clean and lubricate all mechanical linkages. |  |  |  | 0
Check all control wirings and associated fitted components. |  |  |  | 0
Check mechanical operations. |  |  |  | 0
Check the operation of the heaters for the tank. |  |  |  | 0
Check if there is any leak on the tank using SF6 sniffer device. |  |  |  | 0
Record the breaker operations counter reading. |  |  |  | 0
Verify/test gas pressre switch setting (SW1 to SW3) and the 63X function and alarms. |  |  |  | 0
Clean insulators. |  |  |  | 0
Check interrupter pressure relief plates. |  |  |  | 0
Check functionality of kirk key interlock an emergency trip button. |  |  |  | 0
Perform contact resistance test and dynamic resistance measurment. |  |  |  | 0
Perform breaker timing test. |  |  |  | 0
Visually inspect the internal condition of breaker control panel. Ensure all components are working properly. |  |  |  | 0
Perform breaker motion analysis test. |  |  |  | 0
Perform breaker control functional test including alarms, pressure switches, limit switches, etc. |  |  |  | 0
Perform power factor or dissipation factor test on each pole and bushing. |  |  |  | 0
Check for any sign of corona, tracking, ad thermal damages. |  |  |  | 0
Perform breaker trip test (manually and automatically). Visually check the condition of the breaker. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0

## TVSS-E7023-1
OWAM- CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Check for physical damage such as cracks, chips, or corrosion. |  |  |  | 0
Check the torque on all bolts. Tighten as required. |  |  |  | 0
Check the proper rating of the arresters. |  |  |  | 0
Perform insulation resistance/ doble test for leakage current. |  |  |  | 0
Verify that each surge arrester ground lead is individually attached to a ground bus or ground electrode. |  |  |  | 0
Perform bolted connection resistance test. |  |  |  | 0
Clean arrester sheds. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0

## PT-E7023
OWAM - CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Check the condition of PT. Check for any physical damages. |  |  |  | 0
Check the grounding connection. |  |  |  | 0
Check the elibibility of the name plate. |  |  |  | 0
Tighten any loose connection. |  |  |  | 0
Check the fuse condition and verify the size. |  |  |  | 0
Perform IR scan for hot spots. |  |  |  | 0
Perform insulation resistance test. |  |  |  | 0
Perform turns ratio test. |  |  |  | 0
Clean PT as required. |  |  |  | 0
Test oil sample and complete DGA analysis (including H2, C2H2, C2H4, CO, and CH4). |  |  |  | 0
Measure capacitance and dissipation factor and record the finding. |  |  |  | 0
Check for oil leak, read and record pressure gauge reading |  |  |  | 0
Check protective gap. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0

## CT-E7023-A-1
OWAM - CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Conduct visual inspection for any damage. |  |  |  | 0
Perform insulation resistance test of the CT. |  |  |  | 0
Perform thermal (IR) scan. |  |  |  | 0
Tighten any loose connection and check and visible damages. |  |  |  | 0
Clean CT as required. |  |  |  | 0
Perform polarity test. |  |  |  | 0
Perform turn ratio test. |  |  |  | 0
Perform winding resistance test. |  |  |  | 0
Perform excitation test. |  |  |  | 0
Perform burden test. |  |  |  | 0
Check the condition of the nameplate. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0

## CT-E7023-B-1
OWAM - CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Conduct visual inspection for any damage. |  |  |  | 0
Perform insulation resistance test of the CT. |  |  |  | 0
Perform thermal (IR) scan. |  |  |  | 0
Tighten any loose connection and check and visible damages. |  |  |  | 0
Clean CT as required. |  |  |  | 0
Perform polarity test. |  |  |  | 0
Perform turn ratio test. |  |  |  | 0
Perform winding resistance test. |  |  |  | 0
Perform excitation test. |  |  |  | 0
Perform burden test. |  |  |  | 0
Check the condition of the nameplate. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0

## Spare CT-2
OWAM - CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Conduct visual inspection for any damage. |  |  |  | 0
Perform insulation resistance test of the CT. |  |  |  | 0
Perform thermal (IR) scan. |  |  |  | 0
Tighten any loose connection and check and visible damages. |  |  |  | 0
Clean CT as required. |  |  |  | 0
Perform polarity test. |  |  |  | 0
Perform turn ratio test. |  |  |  | 0
Perform winding resistance test. |  |  |  | 0
Perform excitation test. |  |  |  | 0
Perform burden test. |  |  |  | 0
Check the condition of the nameplate. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0

## Spare CT-3
OWAM - CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Conduct visual inspection for any damage. |  |  |  | 0
Perform insulation resistnace test of the CT. |  |  |  | 0
Perform thermal (IR) scan. |  |  |  | 0
Tighten any loose connection and check and visible damages. |  |  |  | 0
Clean CT as required. |  |  |  | 0
Perform polarity test. |  |  |  | 0
Perform turn ratio test. |  |  |  | 0
Perform winding resistance test. |  |  |  | 0
Perform excitation test. |  |  |  | 0
Perform burden test. |  |  |  | 0
Check the condition of the nameplate. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0

## TVSS-E7023-2
OWAM - CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Check for physical damage such as cracks, chips, or corrosion. |  |  |  | 0
Check the torque on all bolts. Tighten as required. |  |  |  | 0
Check the proper rating of the arresters. |  |  |  | 0
Perform insulation resistance/ doble test for leakage current. |  |  |  | 0
Verify that each surge arrester ground lead is individually attached to a ground bus or ground electrode. |  |  |  | 0
Perform bolted connection resistance test. |  |  |  | 0
Clean arrester sheds. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0

## CT-E7023-B-3
OWAM - CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Conduct visual inspection for any damage. |  |  |  | 0
Perform insulation resistance test of the CT. |  |  |  | 0
Perform thermal (IR) scan. |  |  |  | 0
Tighten any loose connection and check and visible damages. |  |  |  | 0
Clean CT as required. |  |  |  | 0
Perform polarity test. |  |  |  | 0
Perform turn ratio test. |  |  |  | 0
Perform winding resistance test. |  |  |  | 0
Perform excitation test. |  |  |  | 0
Perform burden test. |  |  |  | 0
Check the condition of the nameplate. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0

## CT-E7023-A-3
OWAM - CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Conduct visual inspection for any damage. |  |  |  | 0
Perform insulation resistnace test of the CT. |  |  |  | 0
Perform thermal (IR) scan. |  |  |  | 0
Tighten any loose connection and check and visible damages. |  |  |  | 0
Clean CT as required. |  |  |  | 0
Perform polarity test. |  |  |  | 0
Perform turn ratio test. |  |  |  | 0
Perform winding resistance test. |  |  |  | 0
Perform excitation test. |  |  |  | 0
Perform burden test. |  |  |  | 0
Check the condition of the nameplate. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0

## XFMR-E7023
OWAM - CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Check the condition of the bushings, the capacitance and PF value against the nameplate. |  |  |  | 0
Check the operation of cooling fans. |  |  |  | 0
Perform a visual inspection of insulators for evidence of contamination or flashover. |  |  |  | 0
Test the oil sample for dielectric strength and water content. |  |  |  | 0
Test oil sample for complete DGA (including H2, C2H2, C2H4, CO, and CH4). |  |  |  | 0
Check DGA monitor (Calisto 2) for hydrogen, moisture, and CO. |  |  |  | 0
Download the databank and event log of the DGA monitor (Calisto 2) and send them to Morgan Schaffer for evaluation of the monitor. |  |  |  | 0
Check for any corrosion, paint chips, and other damages around the transformer. |  |  |  | 0
Perform visual inspection for insulators for evidence of contamination or flashover and clean insulators. |  |  |  | 0
Check the control cabinets for any sign of damages. |  |  |  | 0
Check the grounding connections. |  |  |  | 0
Conduct inspection inside the OLTC cabinet to ensure everything is functioning properly such as nothing is loose. |  |  |  | 0
Check OLTC cabinet to ensure it has proper oil level. |  |  |  | 0
Check OLTC to ensure the motor is working properly. |  |  |  | 0
Check OLTC to ensure the cabinet heater is working properly. |  |  |  | 0
Check OLTC to ensure the breather is in proper condition. |  |  |  | 0
Check the condition of radiators. |  |  |  | 0
Perform full internal inspection of the control cabinets devices (such as heaters, etc.) including OLTC panel, operating OLTC for full range, performing insulation test, & ratio check. |  |  |  | 0
Perform winding resistance test. |  |  |  | 0
Perform insulation resistance test (PI) |  |  |  | 0
Perform tan δ test. |  |  |  | 0
Perform SFRA. |  |  |  | 0
Perform Power factor test. |  |  |  | 0
Perform turn ratio test. |  |  |  | 0
Clean the bushings. |  |  |  | 0
Perform megger core/ core-ground test. |  |  |  | 0
35. Perform as-left tests and record the findings. |  |  |  | 0

## NGR-E7023
OWAM - CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Conduct visual inspection to the enclosure for any sign of damage. |  |  |  | 0
Keep the NGR clean of accumulate dust or debris. |  |  |  | 0
Disconnect and Isolate the electrical system being grounded through the NGR and open the connection between the system neutral and the Neautral Grounding Resistor. |  |  |  | 0
Conduct a visual inspection of all the parts for any sign of damages. |  |  |  | 0
Check for cracked insulators or busings. |  |  |  | 0
Check the resistive element for continutity. |  |  |  | 0
Check all the internal connections for tightness. |  |  |  | 0
Check the wiring for signs of damage from heat or overloads. |  |  |  | 0
Perform insulation resistance test. |  |  |  | 0
Perform resistance tests. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0

## CT-E7023-1
OWAM - CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Conduct visual inspection for any damage. |  |  |  | 0
Perform insulation resistance test of the CT. |  |  |  | 0
Perform thermal (IR) scan. |  |  |  | 0
Tighten any loose connection and check and visible damages. |  |  |  | 0
Clean CT as required. |  |  |  | 0
Perform polarity test. |  |  |  | 0
Perform turn ratio test. |  |  |  | 0
Perform winding resistance test. |  |  |  | 0
Perform excitation test. |  |  |  | 0
Perform burden test. |  |  |  | 0
Check the condition of the nameplate. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0

## XFMR-E7121
OWAM - CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Inspect all exposed surfaces for evidence of tampering, battered metal, gouges, etc. |  |  |  | 0
Inspect drain cocks, plugs, fuse mountings, and switches for any evidence of insulating liquid seepage around tank-wall gaskets, seals, etc. |  |  |  | 0
Check tank exterior for signs of a leak. |  |  |  | 0
Walk around unit and listen for abnormal noises. |  |  |  | 0
Verify that transformer is not tilted more than 5 degree from horizontal. |  |  |  | 0
Check if there is unusual odors and oil spots around transformer. |  |  |  | 0
Check the operation of vacuum pressure gauge & record the reading. |  |  |  | 0
Check the operation of liquid temp. gauge & record the reading. |  |  |  | 0
Visually inspect the fuses if the fuses are present. |  |  |  | 0
Check for paint chips and eligibility of nameplate. |  |  |  | 0
Check the cable connections. If there are signs of overheating, check for loose connections or discolored spades (paddles). |  |  |  | 0
Check condition of the HV and LV bushings. Observe for any indication of dirt, leakage, breakage, general damage, heat damage or flashover, and clean the bushings. |  |  |  | 0
Check the cubicle Padlock. (if present). |  |  |  | 0
Check for excessive cable weight or stiff cable conductors putting upward or downward pressure on the bushings due to pad settling. |  |  |  | 0
Check the operation of pressure Relief valve and for dirt & debris. |  |  |  | 0
Test oil sample for complete DGA (iincluding H2, C2H2, C2H4, CO, and CH4). |  |  |  | 0
Check ground connection. |  |  |  | 0
Check the operation of winding temp. gauge & record the reading. |  |  |  | 0
Perform turn ratio test. |  |  |  | 0
Perform winding resistance test. |  |  |  | 0
Perform insulation resistance test (PI). |  |  |  | 0
Perform tan δ test. |  |  |  | 0
Perform SFRA. |  |  |  | 0
Check the condition of radiators. |  |  |  | 0
Perform Power Factor test. |  |  |  | 0
Perform megger core/ core-ground test. |  |  |  | 0
Perform full internal inspection of the control cabinets devices (such as heaters, etc.) including LTC panel, operating LTC for full range, performing insulation test, & ratio check. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0

## CT-7121-1
OWAM - CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Conduct visual inspection for any damage. |  |  |  | 0
Perform insulation resistnace test of the CT. |  |  |  | 0
Perform thermal (IR) scan. |  |  |  | 0
Tighten any loose connection and check and visible damages. |  |  |  | 0
Clean CT as required. |  |  |  | 0
Perform polarity test. |  |  |  | 0
Perform turn ratio test. |  |  |  | 0
Perform winding resistance test. |  |  |  | 0
Perform excitation test. |  |  |  | 0
Perform burden test. |  |  |  | 0
Check the condition of the nameplate. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0

## NGR-E7121
OWAM - CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Conduct visual inspection to the enclosure for any sign of damage. |  |  |  | 0
Keep the NGR clean of accumulate dust or debris. |  |  |  | 0
Disconnect and Isolate the electrical system being grounded through the NGR and open the connection between the system neutral and the Neautral Grounding Resistor. |  |  |  | 0
Conduct a visual inspection of all the parts for any sign of damages. |  |  |  | 0
Check for cracked insulators or busings. |  |  |  | 0
Check the resistive element for continutity. |  |  |  | 0
Check all the internal connections for tightness. |  |  |  | 0
Check the wiring for signs of damage from heat or overloads. |  |  |  | 0
Perform insulation resistance test. |  |  |  | 0
Perform resistance tests. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0

## CT-E7121-2
OWAM - CONTRACT SERVICE INFORMATION
Maintenance Items | Name of Employee(s) that Worked on the Maintenance Item | Maintenance Hours Spent on Item | Maintenance Rate per Hour | Total Fees for the Item | Start Date | End Date
Conduct visual inspection for any damage. |  |  |  | 0
Perform insulation resistance test of the CT. |  |  |  | 0
Perform thermal (IR) scan. |  |  |  | 0
Tighten any loose connection and check and visible damages. |  |  |  | 0
Clean CT as required. |  |  |  | 0
Perform polarity test. |  |  |  | 0
Perform turn ratio test. |  |  |  | 0
Perform winding resistance test. |  |  |  | 0
Perform excitation test. |  |  |  | 0
Perform burden test. |  |  |  | 0
Check the condition of the nameplate. |  |  |  | 0
Perform as-left tests and record the findings. |  |  |  | 0